## FCP INDEX
Version #8 -CC&GW/ BWE71
This version 8.85 introduced on 12 April 2017
Customer has requested change to FCP9030 Molex location for all future installations
Openreach Flexible Co-mingling Product (FCP) Matrix
Click on the FCP numbers below to find illustrative layout diagrams and build details. On each diagram in cell B2 you will find the link back to the FCP index. |  | Please note: layouts shown are indicative and reflect the products as 'stand alone'in straight, single-suite layouts. Please note that actual layouts may differ due to site specific conditions. | Click to link for Recifier Alarm & Current Settings
Please note : for AC only products please refer to the APO order or job pack for the initial max and future expected maximum power requirements as well as the AC type |  |  | At-a-glance 'what is it' guide
FCP # | Change control amendment date | Summary of change / amendment relative to previous issue | AC only | Expected future max power | No of Power Base Cabinets | Size of Power Base Cabinet(s) | No of RSU spaces | Size of RSU space(s) | No of CUC in RSU spaces | Max no of ties | HDF Sub-Racks in Power Base | HDF Rack(s) | Expanded Battery Capacity Cabinet | Additional information
FCP0001 |  |  | Y |  | 1 | 600Wx800D | 0 |  | 0 | 6 | Y |  |  | No lockable doors requested
FCP0019 | 2016-05-17 | Template added |  | 9.0kW | 1 | 600Wx600D | 6 | 600Wx600D |  | 54 |  | 1
FCP0049 | 2013-05-07 | Template added |  | 4.0kW | 1 | 600Wx600D | 1 | 600Wx600D | 1 | 0 | N
FCP0063 | 2013-02-13 | Initial and expected maximum power levels corrected |  | 1.5kW | 1 | 600Wx800D | 0 |  | 0 | 3 | Y
FCP0209 |  |  |  | 10.0kW | 1 | 800Wx800D | 3 | 800Wx800D | 3 | 0
FCP0259 | 13 Jan 2013 | Hyper link correction |  | 4.5kW | 1 | 600Wx600D | 1 | 600Wx600D | 0 | 24 | N |  |  | Ties to terminate in customer owned cabinet
FCP0282 | 2014-08-15 | Template created. |  | 6.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0 | N |  |  | Inverters only in Power Base #1
FCP0394 | 2016-08-25 | Template created. |  | 8.0kW | 1 | 800Wx800D | 2 | 800Wx800D | 2 | 0
FCP0547 |  |  |  | 3.1kW | 1 | 800Wx600D | 2 | 600Wx600D | 0 | 18 | Y
FCP0613 |  |  |  | 10.0kW | 1 | 800Wx800D | 3 | 800Wx800D | 3 | 0
FCP0666 | 16 Jan 2013 | Template created. |  | 4.0kW | 1 | 600Wx800D | 2 | 600Wx800D | 2 | 0
FCP0689 | 2014-06-25 | Template added |  | 9.0kW | 1 | 600Wx600D | 6 | 600Wx600D |  | 54 |  | 1
FCP0704 | 2015-01-19 | Template added (Non ESS option for FCP4189) |  | 4.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0 | N |  |  | Non ESS option for FCP4189
FCP0772 |  |  |  | 4.5kW | 1 | 600Wx800D | 2 | 600Wx800D | 0 | 21 | N |  |  | Ties to terminate in customer owned cabinet
FCP0805 | 2013-06-11 | Template added |  | 6.0kW | 1 | 600Wx600D | 3 | 600Wx600D | 0 | 0
FCP0954 | 2013-08-15 | Template added |  | 4.0kW | 1 | 600Wx600D | 0 |  | 0 | 0
FCP1061 | 2015-08-12 | Template corrected to reflect change of max power requirements |  | 3.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0 | N
FCP1213 |  |  |  | 4.5kW | 1 | 800Wx800D | 2 | 800Wx800D | 1 | 0
FCP1222 | 2016-07-18 | Template added | Y |  | 1 | 600Wx800D | 0 |  | 0 | 0 | N
FCP1282 | 2013-12-09 | Template added | Y |  | 1 | 600Wx600D | 0 |  | 0 | 3 | Y
FCP1318 | 2014-07-14 | Template added |  | 4.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0 | N
FCP1327 | 2013-04-30 | Template added |  | 2.0kW | 1 | 600Wx800D | 0 | 600Wx800D |  | 3 | Y
FCP1421 | 2013-07-08 | MDF ties numbering has been modified to reflect customers request |  | 10.1kW | 2 | 600Wx600D | 3 | 600Wx600D | 0 | 27 | N | 1
FCP1422 | 2013-02-14 | Customer confirmation of MCB configuration |  | 1.6kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 12 | Y
FCP1548 | 2014-01-02 | Version 2 "customer order requirement changed to unmetered | Y |  | 1 | 600Wx800D | 0 | 600Wx800D | 0 | 6 | Y |  |  | Version 2 "customer order requirement changed to unmetered
FCP1587 | 2015-12-02 | Single power base cabinet (1500VA n+1 inverter option) for PoP consolidation |  | 10.0kW | 1 | 600Wx600D | [7 empty] | FMC1000 Single Power Base Cabinet for PoP Consolidations
FCP1733 | 2013-02-12 | Template added |  | 0.5kW | 1 | 600Wx600D | 0 |  | 0 | 1 | Y
FCP1768 |  |  | Y |  | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 6 | Y
FCP1853 | 2013-02-12 | Template added |  | 2.0kW | 1 | 600Wx800D | 0 |  | 0 | 5 | Y
FCP2003 | 2013-06-24 | Template added |  | 12.1kW | 2 | 600Wx800D | 5 | 600Wx800D | 0 | 42 | N | 1 |  | Non ESS product ( additional spaces provided for future EBC)
FCP2059 | 2014-01-02 | Version 2 "customer order requirement changed to unmetered | Y |  | 1 | 600Wx800D | 0 |  | 0 | 0 |  |  |  | Version 2 "customer order requirement changed to unmetered
FCP2096 | 2014-06-26 | Template added |  | 9.0kW | 1 | 600Wx600D | 6 | 600Wx600D |  | 54 |  | 1
FCP2182 | 2014-08-15 | Template added | Y |  | 1 | 800Wx800D | 0 |  |  | 6
FCP2201 | 2013-11-20 | Template added |  | 2.0kW | 1 | 600Wx600D | 0 |  | 0 | 3 | Y
FCP2234 |  |  |  | 2.5kW | 1 | 600Wx600D | 2 | 600Wx600D | 0 | 6 | Y
FCP2264 | 2013-12-02 | Template added - HDF Subrack configuration changed |  | 3.0kW | 1 | 800Wx600D | 1 | 600Wx600D |  | 18 | Y
FCP2266 | 2013-10-01 | Template Added Non ESS option for FCP9817 ***New Components corrected |  | 6.0kW | 1 | 800Wx800D | 2 | 800Wx800D | 2 | 0 |  |  | 1 | Non ESS option for FCP9817
FCP2438 | 2014-10-23 | Template added |  | 6.0kW | 1 | 800Wx800D | 1 | 800Wx800D | 1 | 0 | N
FCP2489 | 2013-05-07 | Template added | Y |  | 1 | 600Wx800D | 0 |  | 0 | 0 |  |  |  | No lockable doors requested
FCP2514 | 2013-03-05 | Template added (default MCB settings) |  | 4.0kW | 1 | 800Wx800D | 0 |  | 0 | 6 | Y
FCP2536 | 2016-03-14 | Template added |  | 2.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0
FCP2560 | 2016-06-23 | Template added | Y |  | 1 | 600Wx800D | 0 |  |  | 3
FCP2660 | 2014-06-05 | Template added |  | 2.0kW | 1 | 600Wx800D | 0 |  | 0 | 0 | N
FCP2695 | 2016-08-15 | Template added |  | 4.0kW | 1 | 600Wx600D | 1 | 600Wx600D | 0 | 0 | N
FCP2750 | 2015-08-12 | Template corrected to reflect change of max power requirements |  | 3.0kW | 1 | 600Wx800D | 2 | 600Wx800D | 1 | 0 | N
FCP2788 | 2013-03-27 | Template added |  | 6.0kW | 1 | 600Wx600D | 2 | 600Wx600D | 2 | 0
FCP2851 | 2015-08-20 | Template Added |  | 2.0kW | 1 | 600Wx600D | 0 |  | 0 | 0 | N
FCP2883 | 2014-02-24 | Template added - Corrected inverter details |  | 2.0kW | 1 | 800Wx800D | 1 | 800Wx800D | 1 | 6 | Y
FCP2906 | 2016-03-21 | Template added |  | 2.0kW | 1 | 800Wx800D | 0 |  | 0 |  | N
FCP3112 |  |  | Y |  | 1 | 600Wx800D | 0 |  | 0 | 3 | Y
FCP3389 | 2014-01-14 | Template added |  | 3.0kW | 1 | 600Wx800D | 2 | 600Wx800D | 2 | 6 | Y
FCP3468 | 2013-01-28 | Amended to include lockable door option. | Y |  | 1 | 600Wx800D | 1 |  | 0 | 0
FCP3476 | 10th February 2014 | Template added (corrected) |  | 3.0kW | 1 | 600Wx800D | 3 | 600Wx800D | 3 | 0
FCP3505 |  | Note: Where APO survey results in Non-ESS AC mains then FCP 9101 shall be offered |  | 4.5kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 21 | N |  |  | Ties to terminate in customer owned cabinet
FCP3564 | 2014-10-30 | Template added |  | 6.0kW | 1 | 800Wx800D | 0
FCP3573 | 2014-12-11 | Template added |  | 2.0kW | 1 | 600Wx800D | 0 |  | 0 | 0 | N
FCP3594 | 2014-01-16 | Template added - Non-ESS option for FCP2264 |  | 3.1kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 18 | Y
FCP3621 | 2013-08-15 | Template added |  | 4.0KkW | 1 | 800Wx800D | 2 | 800Wx800D | 2 | 0
FCP3680 | 2015-05-05 | Template added |  | 2.0kW | 1 | 600Wx600D | 0 |  | 0 | 0
FCP3684 | 2014-11-11 | Template added | Y |  | 1 | 600Wx600D | 0 |  |  | 6 | Y
FCP3878 | 2015-06-10 | Template added |  | 6.0kW | 1 | 800Wx800D | 1 | 800Wx800D | 1 | 0 | N
FCP3912 |  |  |  | 4.5kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 9 | Y
FCP3938 |  |  |  | 4.5kW | 1 | 800Wx800D | 2 | 800Wx800D | 1 | 0
FCP3983 | 2013-03-25 | Template added |  | 6.1kW | 1 | 800Wx600D | 2 | 600Wx600D | 0 |  |  |  |  | Ties to terminate in customer owned cabinet
FCP4006 | 2013-05-09 | Template added |  | 3.1kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 19 | Y
FCP4048 | 2013-12-05 | Template added |  | 20kW | 2 | 800Wx800D | 6 | 800Wx800D | 6 | 0 | N |  |  | MCB customisation required at each Power Base Cabinet
FCP4189 | 2014-12-11 | Template added |  | 2.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0 | N
FCP4195 | 2015-02-19 | Template added - Alternative to FCP7791 with all 63A MCB's |  | 4.5kW | 1 | 600Wx600D | 3 | 600Wx600D | 0 | 33 | N | 1
FCP4284 |  |  |  | 6.1kW | 1 | 800Wx800D | 2 | 800Wx800D | 2 | 0
FCP4342 | 2015-03-31 | Template added (Alternative to FCP7648 with all 63A MCB's) |  | 9.0kW | 1 | 600Wx600D | 4 | 600Wx600D | 0 | 54 | N | 1
FCP4415 | 2016-06-06 | Template added |  | 6.0kW | 1 | 800Wx600D | 1 | 600Wx600D | 1 | 3 | N
FCP4482 | 2016-05-13 | Template added |  | 6.0kW | 1 | 600Wx600D | 0
FCP4509 |  |  |  | 3.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0
FCP4521 | 2016-06-30 | Template added | Y |  | 1 | 600Wx600D | 0
FCP4549 |  |  | Y |  | 2 (Dual) | 600Wx800D | 4 | 600Wx800D | 4 | 0
FCP4564 | 2016-07-04 | Template added |  | 12.0kW | 2 (Dual) | 600Wx600D | 6 | 600Wx600D | 0 | 0
FCP4750 |  |  |  | 2.0kW | 1 | 600Wx800D | 2 | 600Wx800D | 0 | 6 | Y
FCP4770 |  |  |  | 10.1kW | 2 | 600Wx800D | 2 | 600Wx800D | 0 | 0
FCP5036 |  |  |  | 3.0kW | 1 | 600Wx800D | 2 | 600Wx800D | 2 | 0
FCP5103 | 2013-03-26 | Template added | Y |  | 1 | 600Wx800D | 0 | 600Wx800D | 0 | 3 | Y |  |  | Dual Door additional security Power Base Cabinet
FCP5156 | 2016-06-14 | Template added |  | 6.0kW | 1 | 600Wx600D | 0 | [6 empty] | Single Power Base Cabinet for PoP Consolidations
FCP5262 | 2016-05-26 | Template added | Y | 5.0kW | 1 | 800Wx800D | 1 | 800Wx800D | 0 | 0 | N
FCP5270 | 2014-08-11 | Template added |  | 2.0kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 12 | Y |  |  | FCP1422 with changes to MCB ratings
FCP5293 | 2014-03-18 | Template added |  | 3.0kW |  | 600Wx800D | 1 | 600Wx800D | 1 | 0
FCP5364 | 2016-07-27 | Additional sub rack configuration option ammended. | Y |  | 1 | 600Wx800D | 0 |  | 0 | 6 | Y
FCP5397 | 2016-07-13 | Template added (Modified) |  | 10.0kW | 2 (Dual) | 600Wx600D | 6 | 600Wx600D | 0 | 0 | N
FCP5441 | 2013-05-07 | Template added | Y |  | 1 | 600Wx800D | 0 |  | 0 | 0
FCP5471 | 2013-04-19 | HDF Type 18e |  |  | 0 | 800Wx600D | 0 |  | 0 | 54 | N | 1 |  | Stand alone HDF Type 18e
FCP5547 | 2014-02-10 | Template added |  | 10.0kW | 1 | 800Wx800D | 3 | 800Wx800D | 1 | 0 | N
FCP5642 | 2016-10-27 | Template added |  | 6.0kW | 1 | 600Wx800D | 0 |  | 0 | 0
FCP7548 | 17 June 20016 | Template added |  | 10.0kW | 1 | 600Wx600D | 6 | 600Wx600D | 0
FCP5554 | 2015-12-02 | Twin Power Base Cabinets (1500VA n+1 inverter option) for PoP consolidation |  | 20.0W | 2 | 600Wx600D | [7 empty] | FCM0012 Two x Power Base Cabinets for POP consolidation
FCP5605 |  |  | Y |  | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0
FCP5834 | 2013-10-09 | Template added |  | 2.0kW | 1 | 600Wx600D | 0 |  |  | 3 | Y
FCP5979 | 23 Spetember 2013 | MDF ties numbering has been changed to reflect customers request |  | 10.1kW | 2 | 600Wx800D | 5 | 600Wx800D | 0 | 21 | N | 1
FCP6030 | 2013-04-19 | HDF Type 9e |  |  | 0 | 800Wx600D | 0 |  | 0 | 27 | N | 1 |  | Stand alone HDF Type 9e
FCP6171 | 2014-01-20 | Template added |  | 1.7kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 15 | Y
FCP6176 | 2015-01-05 | Template added |  | 2.0kW | 1 | 600Wx800D | 0 |  | 0 | 3 | Y |  |  | FCP0063 with additional 6-way (3 pin) AC PDU
FCP6191 | 2014-01-13 | Template added |  | 3.0kW | 1 | 800Wx800D | 1 | 800Wx800D | 1 | 6 | Y
FCP6271 | 2013-12-04 | Template added |  | 3.0kW | 1 | 600Wx800D | 0 |  | 0 | 6 | Y
FCP6386 | 2013-11-22 | Template added | Y |  | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 2 | Y
FCP6516 | 2013-03-26 | Template added |  | 4.0kW | 1 | 600Wx600D | 2 | 600Wx600D | 2
FCP6615 | 2016-07-14 | Template added |  | 3.0kW | 1 | 600Wx600D | 0
FCP6620 | 2015-01-27 | Template added |  | 2.0kW | 1 | 600Wx600D | 1 | 600Wx800D | 1 | 0 | N
FCP6723 | 2014-01-14 | Template added Non-ESS for FCP1422 |  | 3.1kW | 1 | 800Wx600D | 1 | 600Wx600D |  | 10 | Y |  |  | Non ESS option to FCP1422
FCP6743 | 2016-11-21 | Deleted Now revised Template can be found on FCP Matrix B |  | 4.0kW | 1 | 800Wx800D | 0
FCP6842 | 2014-01-14 | Template added |  | 3.1kW | 1 | 800Wx600D | 1 | 600Wx600D |  | 10 | Y
FCP6906 | 2014-12-03 | Template added |  | 2.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 6 | Y
FCP6934 | 2015-11-20 | Template added | Y |  | 2 | 600Wx600D | 4 | 600Wx600D | 0 | 0 | N
FCP6936 | 2015-01-19 | Template added (Non ESS option for FCP3573) |  | 4.0kW | 1 | 600Wx800D | 0 |  | 0 | 0 | N |  |  | Non ESS option for FCP3573
FCP6968 | 2014-05-21 | Template added (corrected) |  | 6.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 3 | Y
FCP7050 | 2013-02-12 | Template modified to reflect an alternative location of HDF Sub rack if requested | Y |  | 1 | 800Wx800D | 0 |  | 0 | 1 | Y
FCP7089 | 2015-02-23 | Template added |  | 4.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0 | N
FCP7094 | 2013-04-19 | HDF Type 9Se (slimline) |  |  | 0 | 800Wx300D | 0 |  | 0 | 27 | N | 1 |  | Stand alone HDF Type 9Se (slimline)
FCP7102 | 2014-04-04 | Template added |  | 2.0kW | 1 | 800Wx600D | 0 |  | 0 | 12 | Y
FCP7326 |  |  | Y |  | 2 (Dual) | 600Wx800D | 2 | 600Wx800D | 2 | 0
FCP7417 | 2016-05-16 | Template added (modified) |  | 6.0kW | 1 | 600Wx800D | 0 |  | 0 | 0
FCP7648 | 11-Dec-2012 | Modified in-flight at customer request to 14 x 63A MCB fitment |  | 9.0kW | 1 | 600Wx600D | 4 | 600Wx600D | 0 | 54 | N | 1
FCP7664 | 2013-07-24 | MDF ties numbering has been modified to reflect customers request |  | 10.1kW | 2 | 800Wx800D | 3 | 600Wx800D | 0 | 21 | Y
FCP7707 | 2013-04-22 | Template added |  | 6.1kW | 1 | 600Wx600D | 2 | 600Wx600D | 0 | 21 | N | 1 |  | Non ESS product
FCP7791 | 11-Dec-2012 | MCB rating changed to default settings - option for all 63A refer to FCP4195 |  | 4.5kW | 1 | 600Wx600D | 3 | 600Wx600D | 0 | 33 | N | 1
FCP7805 | 2013-03-26 | Customer has requested MDF ties to be installed only on the front of the HDF from bottom upwards and ties numbered from left to right - Template has been modified to reflect this |  | 10.1kW | 2 | 600Wx600D | 5 | 600Wx600D | 0 | 21 | N | 1
FCP7836 | 2013-11-07 | Template added |  | 2.0kW | 1 | 600Wx800D | 0 |  | 0 | 0 | N
FCP7885 | 2016-04-29 | Template added | Y | 4.0kW | 1 | 800Wx800D | 0 |  | 0 | 0 | N
FCP8166 | 2015-09-15 | Template added |  | 6.0kW | 1 | 800Wx800D | 2 | 800Wx800D | 1 | 0 | N
FCP8201 |  |  |  | 10.0kW | 1 | 600Wx600D | 7 | 600Wx600D | 0 | 48 | N | 1
FCP8226 | 2013-04-04 | Template added |  | 6.2kW | 1 | 600Wx600D | 2 | 600Wx600D | 2 | 0 | N
FCP8230 | 2013-05-20 | MDF tie cables numbering on HDF changed to reflect customer requirements. |  | 10.1kW | 2 | 600Wx800D | 5 | 600Wx800D | 0 | 19 | N | 1
FCP8297 | 2015-09-24 | Bespoke Template added (RSU2 is 800Wx1000D) with 21CN CuC |  | 4.0kW | 1 | 800Wx800D | 2 | 800Wx800D | 2 | 0 | N |  |  | Bespoke product RSU 2 800Wx1000D with 21 CN Cabinet (CuC)
FCP8407 | 2013-03-25 | Template added |  | 4.0kW | 1 | 600Wx600D | 1 | 600Wx600D | 1 | 0
FCP8426 |  |  |  | 2.0kW | 1 | 600Wx600D | 0 |  | 0 | 0
FCP8474 |  |  | Y |  | 1 | 800Wx800D | 0 |  | 0 | 0
FCP8580 | 2013-01-25 | Template added |  | 4.0kW | 1 | 600Wx800D | 2 | 600Wx800D | 2 | 3 | Y
FCP8597 |  |  | Y |  | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 3 | Y
FCP8804 | 2014-04-07 | Template added |  | 10.0kW | 1 | 800Wx800D | 2 | 800Wx800D | 2 | 0
FCP8821 | 2013-01-23 | Created as an alternative to FCP0209 due to site space availability |  | 10.0kW | 1 | 800Wx800D | 2 | 800Wx800D | 2 | 0
FCP9005 | 2014-11-18 | Templated added |  | 2.0kW | 1 | 600Wx800D | 0 |  | 0 | 0 | N
FCP9030 | 2016-11-01 | Template added (Molex in CuC location changed for all future installation) |  | 4.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0 | N
FCP9052 | 2013-03-11 | Template added |  | 6.0kW | 1 | 800Wx600D | 2 | 600Wx600D | 2 | 0
FCP9069 | 2013-04-29 | Template added | Y |  | 1 | 600Wx800D | 0 |  | 0 | 0
FCP9091 | 2013-01-28 | Template added |  | 4.5kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 21 | Y
FCP9101 |  | Offered instead of FCP3505 where Non-ESS power is necessary (See LTDP ref ADW) |  | 6.1kW | 1 | 800Wx600D | 1 | 600Wx600D | 0 | 21 | N |  |  | Ties to terminate in customer owned cabinet
FCP9128 | 2013-01-28 | Includes lockable door on AC only Power Base | Y |  | 2 (Dual) | 600Wx600D | 0 |  | 0 | 0
FCP9140 | 2013-01-28 | Non-ESS alternative to FCP9269 - Maximum MDF tie capacity is18 |  | 6.1kW | 1 | 800Wx600D | 2 | 600Wx600D | 0 | 18 | Y
FCP9148 | 2016-06-15 | Template added |  | 3.0kW | 1 | 800Wx800D | 0
FCP9158 | 2016-05-13 | Template added |  | 2.0kW | 1 | 600Wx800D | 0
FCP9180 |  |  |  | 2.0kW | 1 | 800Wx800D | 0 |  | 0 | 3 | Y
FCP9227 | 2014-12-02 | Templated added (Non ESS of FCP0666) |  | 4.0kW | 1 | 600Wx800D | 2 | 600Wx800D | 2 | 0 | N |  | 1 | Non ESS for FCP0666
FCP9258 | 2014-06-16 | Template added |  | 2.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 0 | 0 | N
FCP9261 |  |  |  | 10.0kW | 1 | 800Wx800D | 3 | 800Wx800D | 3 | 0
FCP9269 | 3 January 2013 | HDF subframe configuration and ties numbering to suit customer request |  | 4.5kW | 1 | 800Wx600D | 2 | 600Wx600D | 0 | 21 | Y
FCP9372 | 2014-02-10 | Template added (corrected) |  | 2.0kW | 1 | 800Wx600D | 1 | 600Wx600D |  | 12 | Y
FCP9591 | 2013-01-31 | Zero LLU tie cable capacity. |  | 4.5kW | 1 | 600Wx600D | 2 | 600Wx600D | 0 | 0
FCP9597 | 2016-01-28 | Template added |  | 3.1kW | 1 | 600Wx800D | 0 |  | 0 | 0 | N
FCP9609 | 2013-03-26 | Template added - VU Numbering corrected | Y |  | 1 | 600Wx600D | 1 | 600Wx600D | 0 | 3 | Y |  |  | Dual Door additional security Power Base Cabinet
FCP9632 | 2016-04-21 | Template added |  | 2.0kW | 1 | 800Wx600D | 0
FCP9646 | 2015-07-02 | Template added HDF Tie cable numering changed at customers request |  | 10.1kW | 2 | 800Wx600D | 5 | 600Wx600D | 0 | 40 |  | 1 |  | MDF Ties number shown as requested by customer
FCP9672 | 2016-05-13 | Template added |  | 6.0kW | 1 | 600Wx600D | 0
FCP9674 |  |  |  | 3.0kW | 1 | 800Wx800D | 1 | 800Wx800D | 0 | 2 | N |  |  | Ties to terminate in customer owned cabinet
FCP9706 | 2015-06-22 | Template added | Y |  | 1 | 600Wx800D | 1 | 600Wx800D
FCP9721 | 2013-01-23 |  |  | 4.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 0 |  |  | 1
FCP9817 |  |  |  | 6.0kW | 1 | 800Wx800D | 2 | 800Wx800D | 2 | 0
FCP9861 | 2013-01-25 |  |  | 4.0kW | 1 | 600Wx800D | 1 | 600Wx800D | 1 | 3 | Y |  | 1
FCP9867 | 2013-03-26 | Template added - VU Numbering corrected | Y |  | 1 | 600Wx600D | 2 | 600Wx600D | 0 | 0 |  |  |  | Dual Door additional security Power Base Cabinet
FCP9937 | 2013-09-17 | FCP9937 subsumes FCP0469 (cancelled on LLUMS) Ties numbering modified |  | 10.1kW | 2 | 800Wx800D | 2 | 600Wx800D | 0 | 21 | Y

## Disclaimer
It should be noted that the information outlined in this slide-pack represents Openreach’s current view at the time of publication. This information may change through further development and feedback.
The purpose of this slide-pack is to provide additional information to support Communications Provider (CP) FCP build planning. It does not represent a finalised definition/specification of the products. Any plans and orders carried out by CPs based on the contents of this slide-pack are entirely at the CP’s own risk.
© British Telecommunications plc 2014

## Templates
Version #5 CC&GW/ BWE253/4thJan2013
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCPxxxx
Power Base Cabinet Size | From dimensioning tool |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [5 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [5 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [56 empty] | Standard superstructure assembly | [5 empty] | Standard superstructure assembly |  |  |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly |  |  |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | From dimensioning tool
Standby AC power | ESS (default) . Non-ESS | AC only Power Base Cabinet 600W x 600D | [6 empty] | AC only Power Base Cabinet 600W x 800D | [5 empty] | AC only Power Base Cabinet 800W x 600D | [6 empty] | AC only Power Base Cabinet 800W x 800D | [5 empty] | Power Base Cabinet 600W x 600D | [6 empty] | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 800W x 600D | [6 empty] | Power Base Cabinet 800W x 800D | [6 empty] | EBC Cabinet 600W x 600D | [5 empty] | EBC Cabinet 600W x 800D | [5 empty] | CuC Cabinet 600W x 600D | [5 empty] | CuC Cabinet 600W x 800D | [5 empty] | CuC Cabinet 800W x 600D | [5 empty] | CuC Cabinet 800W x 800D | [5 empty] | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 800D | [6 empty] | AC only Power Base Cabinet 600W x 600D | [5 empty] | AC only Power Base Cabinet 600W x 800D |  |  |  |  | AC only Power Base Cabinet 800W x 600D | [5 empty] | AC only Power Base Cabinet 800W x 800D |  |  |  |  | Power Base Cabinet 600W x 600D | [6 empty] | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 800W x 600D | [6 empty] | Power Base Cabinet 800W x 800D | [6 empty] | EBC Cabinet 600W x 600D |  |  |  |  | EBC Cabinet 600W x 800D |  |  |  |  | CuC Cabinet 600W x 600D |  |  |  |  | CuC Cabinet 600W x 800D |  |  |  |  | CuC Cabinet 800W x 600D |  |  |  |  | CuC Cabinet 800W x 800D |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 800D
Electricity metering | Metered (default) / Un-metered |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  | L | Front view |  |  | R |  |  | L | Front view |  |  | R |  |  | L | Front view |  |  | R |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Front view |  |  | R |  |  | L | Front view |  |  | R |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  | L | Rear view |  |  | R |  |  | L | Rear view |  |  | R |  |  | L | Rear view |  |  | R |  |  | L | Rear view |  |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  | L | rear view |  |  | R |  |  | L | rear view |  |  | R
Initial maximum power capacity | 0.5kW - 20kW in 0.1kW steps
Expected future maximum power capacity | 0.5kW - 20kW in 0.1kW steps
AC Supply type (actual design is subject to BT survey) | From dimensioning tool |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | From dimensioning tool |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 | EBC-C Battery Breaker |  | VU45 |  |  | VU45 | EBC-C Battery Breaker |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45
Rectifiers per DC System | From dimensioning tool |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 | Switchgear |  | VU44 |  |  | VU44 | Switchgear |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | From dimensioning tool |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 | DC Power System Chassis |  |  | VU43 |  |  | VU43 | DC Power System Chassis |  |  | VU43 |  |  | VU43 | DC Power System Chassis |  |  | VU43 |  |  | VU43 | DC Power System Chassis |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 | AC Power Panel & Meter | VU43 |  |  |  | VU43 | AC Power Panel & Meter | VU43 |  |  | VU43 | AC Power Panel & Meter | VU43 |  |  |  | VU43 | AC Power Panel & Meter | VU43 |  |  | VU43 | AC Power Panel & Meter |  |  | VU43 |  |  | VU43 | AC Power Panel & Meter |  |  | VU43 |  |  | VU43 | AC Power Panel & Meter |  |  | VU43 |  |  | VU43 | AC Power Panel & Meter |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | From dimensioning tool |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | From dimensioning tool |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 | Inverter Chassis |  |  | VU40 |  |  | VU40 | Inverter Chassis |  |  | VU40 |  |  | VU40 | Inverter Chassis |  |  | VU40 |  |  | VU40 | Inverter Chassis |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600Wx600D, 600Wx800D, 800Wx800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 | 16-Way Molex DC sub-distribution module |  |  | VU39 |  |  | VU39 | 16-Way Molex DC sub-distribution module |  |  | VU39 |  |  | VU39 | 16-Way Molex DC sub-distribution module |  |  | VU39 |  |  | VU39 | 16-Way Molex DC sub-distribution module |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39 |  |  | VU39 | AC PDU & Flex tie bar |  |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar |  |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar |  |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 0 - 10 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Not required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | Fixing Bar | VU37 |  |  |  | VU37 | Fixing Bar | VU37 |  |  | VU37 | Fixing Bar | VU37 |  |  |  | VU37 | Fixing Bar | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | From dimensioning tool |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | From dimensioning tool |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 0 - 54 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | Up to 54 total |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | Up to 54 total |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | Up to 54 total |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | Up to 54 total |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | Up to number of RSUs |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 | HDF Sub rack # 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0,1,2 per CuC |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0,1,2 per Cuc |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0,1,2 per CuC |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  |  | VU19 |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  | VU19 | HDF Sub rack # 2 |  |  | VU19 |  |  | VU19 | HDF Sub rack # 2 |  |  | VU19 |  |  | VU19 | HDF Sub rack # 2 |  |  | VU19 |  |  | VU19 | HDF Sub rack # 2 |  |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18 |  |  | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18 |  |  | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18 |  |  | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A(default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A(default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | From dimensioning tool |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | From dimensioning tool |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10
|  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8
The templates are drawn as guides, in the AC only power Base Cabinets the customer may specify where they may require HDF sub racks to be installed leaving space for the customer to supply their own batteries. |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6
The Power Base cabinets have been drawn with examples of 1 or 2 or 3 battery strings which will vary depending on the power requirement of the order - the HDF sub racks are shown in the default positions i.e. 1-3 at the front 4-6 at the rear, again this may vary dependant on the customer requirements both in Power Base cabinet or HDF. |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU4 |  |  | VU4 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU4
Remember - a 600wide Power Base Cabinet can take a maximum of 6 MDF tie cables - in the 800 wide Power Base cabinet the maximum number of ties is dependant on the number of battery strings |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Front View | [5 empty] | Front View | [6 empty] | Front View | [5 empty] | Front View | [6 empty] | Front View | [6 empty] | Front View | [6 empty] | Front View | [6 empty] | Front View | [5 empty] | Front View | [5 empty] | Front View | [5 empty] | Front View | [5 empty] | Front View | [5 empty] | Front View | [5 empty] | Front View | [6 empty] | Front View | [6 empty] | Rear View | [5 empty] | Rear View |  |  |  |  | Rear View | [5 empty] | Rear View |  |  |  |  | Rear View | [6 empty] | Rear View | [6 empty] | Rear View | [6 empty] | Rear View | [6 empty] | Rear View |  |  |  |  | Rear View |  |  |  |  | Rear View |  |  |  |  | Rear View |  |  |  |  | Rear View |  |  |  |  | Rear View |  |  |  |  | Rear View | [6 empty] | Rear View
|  | 600mm | [6 empty] | 600mm | [5 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 600mm | [6 empty] | 600mm | [6 empty] | 600mm | [6 empty] | 600mm | [6 empty] | 600mm | [5 empty] | 600mm | [5 empty] | 600mm | [5 empty] | 600mm | [5 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 600mm | [5 empty] | 600mm |  |  |  |  | 800mm | [5 empty] | 800mm |  |  |  |  | 600mm | [6 empty] | 600mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm |  |  |  |  | 800mm |  |  |  |  | 800mm | [6 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
[5 empty] | Power Base Cabinet | [6 empty] | Power Base Cabinet | [5 empty] | Power Base Cabinet | [6 empty] | Power Base Cabinet | [5 empty] | Power Base Cabinet | [6 empty] | Power Base Cabinet | [6 empty] | Power Base Cabinet | [6 empty] | Power Base Cabinet | [12 empty] | EBC Cabinet | [11 empty] | CUC | [11 empty] | CUC | [12 empty] | HDF
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [95 empty] | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
[60 empty] | EBC Cabinet | [11 empty] | CUC | [11 empty] | CUC
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D | [6 empty] | 600W x 800D | [5 empty] | 800W x 600D | [6 empty] | 800W x 800D | [5 empty] | 600W x 600D | [6 empty] | 600W x 800D | [6 empty] | 800W x 600D | [6 empty] | 800W x 800D | [6 empty] | 600W x 600D | [5 empty] | 600W x 800D | [5 empty] | 600W x 600D | [5 empty] | 600W x 800D | [5 empty] | 800W x 600D | [5 empty] | 800W x 800D | [5 empty] | 800W x 600D | [6 empty] | 800W x 800D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts
[8 empty] | End of diagram | [12 empty] | End of diagram | [89 empty] | End of diagram | [10 empty] | End of diagram

## FCP3938
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [18 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3938
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [27 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer RSU (800W x 800D) | [5 empty] | Customer RSU (800W x 800D) |  |  |  | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | RSU2 800W x 800D x 2200H | [5 empty] | RSU2 800W x 800D x 2200H | [5 empty] | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 | [13 empty] | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 | [13 empty] | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 | [13 empty] | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 | [13 empty] | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 | [13 empty] | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 | [13 empty] | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 | [13 empty] | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 | [13 empty] | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | [13 empty] | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 | [13 empty] | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | [13 empty] | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 | [13 empty] | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 | [13 empty] | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 | [13 empty] | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 | [13 empty] | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 | [13 empty] | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 | [13 empty] | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 | [13 empty] | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 | [13 empty] | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 | [13 empty] | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 | [13 empty] | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 | [13 empty] | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 | [13 empty] | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 | [13 empty] | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 | [13 empty] | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 | [13 empty] | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 | [13 empty] | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 | [13 empty] | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 32A |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 | [13 empty] | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 6A |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | [13 empty] | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 6A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 | [13 empty] | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 | [13 empty] | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 | [13 empty] | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 | [13 empty] | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 | [13 empty] | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 | [13 empty] | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 | [13 empty] | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 | [13 empty] | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 | [13 empty] | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 | [13 empty] | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 | [13 empty] | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 | [13 empty] | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 | [13 empty] | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 | [13 empty] | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 | [13 empty] | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 | [13 empty] | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 | [13 empty] | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm | Front view | [5 empty] | Rear view |  |  |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm |  |  |  | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [5 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1 | [7 empty] | RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [5 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8426
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8426
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter provided |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5364
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | Option #1 | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [14 empty] | Option #2 | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5364
Power Base Cabinet Size | 600W x 800D |  |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [8 empty] | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) |  | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D | [8 empty] | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  |  | L | Front view |  |  | R |  |  | L | Rear view |  |  | R |  |  |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  |  | VU45 |  |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter |  |  | VU45 |  |  |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 |  | VU41
[5 empty] | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar |  |  | VU39 |  |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
[5 empty] | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 2 |  |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 6 |  |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 1 |  |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
[5 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  |  |  | VU16 | HDF Sub rack # 2 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  |  |  | VU15 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  | VU14
[5 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  |  |  | VU11 | HDF Sub rack # 1 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  |  |  | VU10 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
Option #1 Default positioning of the HDF Sub racks - Refer to Option # 2 where customer has requested MDF ties to be terminated on HDF Subracks installed on the front in VU7-VU11 and VU12 -VU16 *** Check job pack *** |  |  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
[5 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
[5 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5 |  |  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5 |  | VU5
[5 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU4 |  |  |  |  | VU4 | Space reserved for customers own batteries |  |  | VU4 |  |  |  | VU4 | Space reserved for customers own batteries | VU4
[5 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
[5 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
[5 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  |  | Front View | [6 empty] | Rear view | [8 empty] | Front View | [7 empty] | Rear view
|  |  | 600mm | [6 empty] | 600mm | [8 empty] | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
[7 empty] | Rear | [15 empty] | Rear
FCP AC Panel (used in all Power Base Cabinets)
[7 empty] | Power Base Cabinet | [15 empty] | Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[7 empty] | 600W x 800D | [15 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option | [5 empty] | Front | [15 empty] | Front
[7 empty] | PLAN VIEW | [15 empty] | PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [16 empty] | End of diagram | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3112
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3112
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7648
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [32 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7648
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [24 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [23 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [21 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [19 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [21 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [19 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [21 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [19 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [21 empty] | VU45 | HDF Sub rack # 17 |  |  | VU45 |  |  | VU45 | HDF Sub rack # 18 |  |  | VU45 | [19 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 | [21 empty] | VU44 | MDF Tie # 51 | MDF Tie # 50 | MDF Tie # 49 | VU44 |  |  | VU44 | MDF Tie # 52 | MDF Tie # 53 | MDF Tie # 54 | VU44 | [19 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [21 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [19 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [21 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [19 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [21 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [19 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [21 empty] | VU40 | HDF Sub rack # 15 |  |  | VU40 |  |  | VU40 | HDF Sub rack # 16 |  |  | VU40 | [19 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | EBCL fibre tray |  | VU39 | [21 empty] | VU39 | MDF Tie # 45 | MDF Tie # 44 | MDF Tie # 43 | VU39 |  |  | VU39 | MDF Tie # 46 | MDF Tie # 47 | MDF Tie # 48 | VU39 | [19 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 4 |  |  | VU38 |  |  | VU38 | [21 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [19 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [21 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [19 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [21 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [19 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [21 empty] | VU35 | HDF Sub rack # 13 |  |  | VU35 |  |  | VU35 | HDF Sub rack # 14 |  |  | VU35 | [19 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [21 empty] | VU34 | MDF Tie # 39 | MDF Tie # 38 | MDF Tie # 37 | VU34 |  |  | VU34 | MDF Tie # 40 | MDF Tie # 41 | MDF Tie # 42 | VU34 | [19 empty] | VU34 |  | VU34
HDF Sub racks provided | 18 |  |  | VU33 |  |  | VU33 | [21 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [19 empty] | VU33 |  | VU33
Expected future maximum tie cables | 54 |  |  | VU32 |  |  | VU32 | [21 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [19 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  | VU31 | [21 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [19 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [21 empty] | VU30 | HDF Sub rack # 11 |  |  | VU30 |  |  | VU30 | HDF Sub rack # 12 |  |  | VU30 | [19 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [21 empty] | VU29 | MDF Tie # 33 | MDF Tie # 32 | MDF Tie # 31 | VU29 |  |  | VU29 | MDF Tie # 34 | MDF Tie # 35 | MDF Tie # 36 | VU29 | [19 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [21 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [19 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [21 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [19 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [21 empty] | VU25 | HDF Sub rack # 9 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 10 |  |  | VU25 | [19 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [21 empty] | VU24 | MDF Tie # 27 | MDF Tie # 26 | MDF Tie # 25 | VU24 |  |  | VU24 | MDF Tie # 28 | MDF Tie # 29 | MDF Tie # 30 | VU24 | [19 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [21 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [19 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [21 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [19 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [21 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [19 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [21 empty] | VU20 | HDF Sub rack # 7 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 8 |  |  | VU20 | [19 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3- (all access from front) |  | VU19 | [21 empty] | VU19 | MDF Tie # 21 | MDF Tie # 20 | MDF Tie # 19 | VU19 |  |  | VU19 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU19 | [19 empty] | VU19 | BATTERY ENCLOSURE #3- (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [21 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [19 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [21 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [19 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [21 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [19 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [21 empty] | VU15 | HDF Sub rack # 5 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 6 |  |  | VU15 | [19 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [21 empty] | VU14 | MDF Tie # 15 | MDF Tie # 14 | MDF Tie #13 | VU14 |  |  | VU14 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie #18 | VU14 | [19 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [21 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [19 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [21 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [19 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [21 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [19 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [21 empty] | VU10 | HDF Sub rack # 3 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 4 |  |  | VU10 | [19 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [21 empty] | VU9 | MDF Tie # 9 | MDF Tie # 8 | MDF Tie # 7 | VU9 |  |  | VU9 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU9 | [19 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [21 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [19 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [21 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [19 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [21 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [19 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [21 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5 | [19 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [21 empty] | VU4 | MDF Tie # 3 | MDF Tie # 2 | MDF Tie #1 | VU4 |  |  | VU4 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU4 | [19 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [21 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [19 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [21 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [19 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [21 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [19 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9269
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [17 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9269
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [26 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [20 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [22 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [22 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [22 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  |  | VU44 | [22 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [22 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [22 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [22 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [22 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | HDF sub rack # 5 |  |  | VU39 | [22 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 | MDF tie # 13 | MDF tie # 14 | MDF tie # 15 | VU38 | [22 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [22 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [22 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [22 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 | HDF sub rack # 4 |  |  | VU34 | [22 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 7 |  |  | VU33 | MDF tie # 10 | MDF tie # 11 | MDF tie # 12 | VU33 | [22 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 20 |  |  | VU32 |  |  |  | VU32 | [22 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  |  | VU31 | [22 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [22 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 | HDF sub rack # 3 |  |  | VU29 | [22 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 | MDF tie # 7 | MDF tie # 8 | MDF tie # 9 | VU28 | [22 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [22 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H | [5 empty] | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [22 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 2 |  |  | VU24 | [22 empty] | VU24 | HDF Sub rack # 7 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU23 | [22 empty] | VU23 | MDF Tie # 21 | MDF Tie # 20 | MDF Tie # 19 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [22 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [22 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [22 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [22 empty] | VU19 | HDF Sub rack # 6 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [22 empty] | VU18 | MDF Tie # 18 | MDF Tie # 17 | MDF Tie # 16 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [22 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [22 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [22 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [22 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [22 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [22 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [22 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [22 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [22 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [22 empty] | VU8 |  |  |  | VU8
HDF sub-rack and tie cable provision sequence reflects a specific customer request. The first 15 x MDF tie cables are to be terminated from the front of the Power Base cabinet VU15 upwards to VU39 then ties 16 onwards to be terminated on the rear from VU15 upwards. |  |  |  | VU7 |  |  |  | VU7 | [22 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [22 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [22 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [22 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [22 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [22 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [22 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1 |  |  |  |  | RSU 2
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D |  |  |  |  | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0001
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0001
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Not Required |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 | HDF Sub rack # 2 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 | HDF Sub rack # 1 |  |  | VU10 |  |  |  | VU10 |  | VU10
|  |  |  | VU9 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
Customer has requested that space is left for customer to supply their own batteries between VU1 and VU5 - MDF ties to be terminated from VU6 to VU15 upwards both on the front of the power base cabinet. |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 | Space reserved for customers own batteries |  |  | VU4 |  |  |  | VU4 | Space reserved for customers own batteries | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3505
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [11 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3505
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [12 empty] | Cabler riser for Customer cabling only | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [13 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [13 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [13 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [13 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [13 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [13 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [13 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 | [13 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [13 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [13 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [13 empty] | VU35 |  | VU35
Openreach HDF option requirement | Customer to provide in own cabinet |  |  | VU34 |  |  | VU34 | [13 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [13 empty] | VU33 |  | VU33
Expected future maximum tie cables | 20 |  |  | VU32 |  |  | VU32 | [13 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [13 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [13 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [13 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [13 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [13 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [13 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [13 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [13 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [13 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [13 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [13 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [13 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [13 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | The Power Base Cabinet is to be installed without right hand side panel (when viewed from the front). This will allow the MDF Tie cables to be routed as per dotted lines directly into the customer Combi-MSAN in RSU1 (see diagram above for more details) | [9 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [13 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [13 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [13 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [13 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [13 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [13 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [13 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [13 empty] | VU8 |  | VU8
The Power Base Cabinet is to be supplied without the right hand side panel (when viewed from the front) this will allow the MDF ties to be routed down into the right hand cable riser of the Power Base and then out into the side of the Combi-MSAN cabinet. Cables are tied to the front to back horizontal bars provided. . Note that the customer’s Combi-MSAN has cable access apertures arranged vertically on one side. Note: Where the APO survey finds that use of Non-ESS AC mains is necessary then FCP 9101 shall be offered |  |  |  | VU7 |  |  | VU7 | [13 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [13 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [13 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [13 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [13 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [13 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [7 empty] | PLAN VIEW
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [11 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D |  |  |  |  | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1548
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1548
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45
Number of DC Systems provided | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 | AC Power Panel |  |  | VU44
Rectifiers per DC System | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 | AC PDU & Flex tie bar |  |  | VU40
|  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Customer RSU size | 600W x 800D |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Quantity of Customer RSUs | 0 |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Dual Doors standard |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
|  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
HDF Sub racks provided | 2 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Expected future maximum tie cables | 5 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUT tie cables required | 1 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUL tie cables required | 0 |  |  | VU29 | HDF Sub rack # 1 |  |  | VU29 |  |  |  | VU29 | HDF Sub rack # 2 |  |  | VU29
Initial LLUX tie cables required | 0 |  |  | VU28 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU28 |  |  |  | VU28 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU28
Initial LLUY tie cables required | 0 |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
|  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
Customer Use Cabinets with doors | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
This is a Dual Door cabinet designed to give the customer a higher level of physical security for specific items of equipment within a single cabinet Access Locate / LLU PoP. A horizontal steel bulkhead is used to separate the FCP cabinet into lower and upper compartments. Cable access between the upper and lower compartments is provided using four circular openings fitted with protective grommets.This FCP product is supplied with 'Codelock1000' on the upper doors and no locks on the lower doors - The locks for the lower compartment are supplied and installed by the customer. This will give the customer full control over access to the lower compartment. |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9101
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [11 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9101
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
Standby AC power | Non-ESS | Power Base Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [12 empty] | Cabler riser for Customer cabling only | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [13 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [13 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 5 |  |  | VU44 |  |  | VU44 | [13 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [13 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [13 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [13 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [13 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 | [13 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [13 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [13 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [13 empty] | VU35 |  | VU35
Openreach HDF option requirement | Customer to provide in own cabinet |  |  | VU34 |  |  | VU34 | [13 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [13 empty] | VU33 |  | VU33
Expected future maximum tie cables | 20 |  |  | VU32 |  |  | VU32 | [13 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [13 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [13 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [13 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [13 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [13 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [13 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [13 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [13 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [13 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [13 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [13 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [13 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [13 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | The Power Base Cabinet is to be installed without right hand side panel (when viewed from the front). This will allow the MDF Tie cables to be routed as per dotted lines directly into the customer Combi-MSAN in RSU1 (see diagram above for more details of cabling) | [9 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [13 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [13 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [13 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [13 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [13 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [13 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) |  |  |  | VU9 |  |  | VU9 | [13 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [13 empty] | VU8 |  | VU8
The Power Base Cabinet is to be supplied without the right hand side panel (when viewed from the front) this will allow the MDF ties to be routed down into the right hand cable riser of the Power Base and then out into the side of the Combi-MSAN cabinet. Cables are tied to the front to back horizontal bars provided. . Note that the customer’s Combi-MSAN has cable access apertures arranged vertically on one side. Note: Offered where Non-ESS power is necessary instead of FCP3505. |  |  |  | VU7 |  |  | VU7 | [13 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [13 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [13 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [13 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [13 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [13 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm | Front view | [5 empty] | Rear view |  |  |  |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [11 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D |  |  |  |  | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0063
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0063
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | single line (phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7791
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [27 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7791
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [19 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [19 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [16 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [15 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [16 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [15 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [16 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [15 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [16 empty] | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | [15 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [16 empty] | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 | [15 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [16 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [15 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [16 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [15 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [16 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [15 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [16 empty] | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 | [15 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | EBCL fibre tray |  | VU39 | [16 empty] | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 | [15 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 | [16 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [15 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [16 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [15 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [16 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [15 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [16 empty] | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 | [15 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [16 empty] | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 | [15 empty] | VU34 |  | VU34
HDF Sub racks provided | 11 |  |  | VU33 |  |  | VU33 | [16 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [15 empty] | VU33 |  | VU33
Expected future maximum tie cables | 33 |  |  | VU32 |  |  | VU32 | [16 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [15 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  | VU31 | [16 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [15 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [16 empty] | VU30 | HDF Sub rack # 11 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 | [15 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [16 empty] | VU29 | MDF Tie # 33 | MDF Tie # 32 | MDF Tie # 31 | VU29 |  |  | VU29 |  |  |  | VU29 | [15 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [16 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [15 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [16 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [15 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [16 empty] | VU25 | HDF Sub rack # 9 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 10 |  |  | VU25 | [15 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [16 empty] | VU24 | MDF Tie # 27 | MDF Tie # 26 | MDF Tie # 25 | VU24 |  |  | VU24 | MDF Tie # 28 | MDF Tie # 29 | MDF Tie # 30 | VU24 | [15 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [16 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [15 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [16 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [15 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [16 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [15 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [16 empty] | VU20 | HDF Sub rack # 7 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 8 |  |  | VU20 | [15 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [16 empty] | VU19 | MDF Tie # 21 | MDF Tie # 20 | MDF Tie # 19 | VU19 |  |  | VU19 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU19 | [15 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [16 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [15 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [16 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [15 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [16 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [15 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [16 empty] | VU15 | HDF Sub rack # 5 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 6 |  |  | VU15 | [15 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [16 empty] | VU14 | MDF Tie # 15 | MDF Tie # 14 | MDF Tie #13 | VU14 |  |  | VU14 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie #18 | VU14 | [15 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [16 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [15 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [16 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [15 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [16 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [15 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [16 empty] | VU10 | HDF Sub rack # 3 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 4 |  |  | VU10 | [15 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [16 empty] | VU9 | MDF Tie # 9 | MDF Tie # 8 | MDF Tie # 7 | VU9 |  |  | VU9 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU9 | [15 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [16 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [15 empty] | VU8 |  | VU8
Modified to reflect default MCB settings |  |  |  | VU7 |  |  | VU7 | [16 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [15 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [16 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [15 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [16 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5 | [15 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [16 empty] | VU4 | MDF Tie # 3 | MDF Tie # 2 | MDF Tie #1 | VU4 |  |  | VU4 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU4 | [15 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [16 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [15 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [16 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [15 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [16 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [15 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9261
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [23 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9261
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [36 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer RSU2 (800W x 800D) |  |  |  |  | Customer RSU3 (800W x 800D) | [5 empty] | Customer RSU3 (800W x 800D) |  |  |  | Customer RSU2 (800W x 800D) |  |  |  | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | RSU2 800W x 800D x 2200H |  |  |  |  | RSU3 800W x 800D x 2200H | [5 empty] | RSU3 800W x 800D x 2200H |  |  |  | RSU2 800W x 800D x 2200H | [5 empty] | VU48 |  | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 10 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 | [22 empty] | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 | [22 empty] | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 | [22 empty] | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 | [22 empty] | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 | [22 empty] | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 | [22 empty] | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 | [22 empty] | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 | [22 empty] | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | [22 empty] | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 | [22 empty] | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | [22 empty] | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 | [22 empty] | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 | [22 empty] | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 | [22 empty] | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 | [22 empty] | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 | [22 empty] | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 | [22 empty] | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 | [22 empty] | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 | [22 empty] | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 | [22 empty] | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 | [22 empty] | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 | [22 empty] | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 | [22 empty] | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 | [22 empty] | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 | [22 empty] | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 | [22 empty] | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 | [22 empty] | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 | [22 empty] | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 |  |  | VU19 | [22 empty] | VU19 |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | [22 empty] | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 | [22 empty] | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 | [22 empty] | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 | [22 empty] | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 | [22 empty] | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 | [22 empty] | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 | [22 empty] | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 | [22 empty] | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 | [22 empty] | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 | [22 empty] | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 | [22 empty] | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 | [22 empty] | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 | [22 empty] | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 | [22 empty] | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 | [22 empty] | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 | [22 empty] | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 | [22 empty] | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 | [22 empty] | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm |  |  |  |  | 800mm | [5 empty] | 800mm |  |  |  | 800mm |  |  |  | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [5 empty] | Rear |  |  |  |  | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet in RSU 1 | [7 empty] | RSU 2 |  |  |  |  | RSU 3
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D |  |  |  |  | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [5 empty] | Front |  |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0547
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [17 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0547
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [26 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view | R |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [20 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [22 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [22 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [22 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 | [22 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [22 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [22 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [22 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [22 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | EBCL fibre tray |  |  | VU39 | [22 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  |  | VU38 | [22 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [22 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [22 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [22 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [22 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 6 |  |  | VU33 |  |  |  | VU33 | [22 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 18 |  |  | VU32 |  |  |  | VU32 | [22 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 4 |  |  | VU31 |  |  |  | VU31 | [22 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [22 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 | HDF sub rack # 5 |  |  | VU29 | [22 empty] | VU29 | HDF sub rack # 6 |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 | MDF tie # 13 | MDF tie # 14 | MDF tie # 15 | VU28 | [22 empty] | VU28 | MDF tie # 18 | MDF tie # 17 | MDF tie # 16 | VU28
|  |  |  | VU27 |  |  |  | VU27 | [22 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H | [5 empty] | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [22 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 3 |  |  | VU24 | [22 empty] | VU24 | HDF Sub rack # 4 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU23 | [22 empty] | VU23 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [22 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [22 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [22 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [22 empty] | VU19 | HDF Sub rack # 2 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [22 empty] | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [22 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [22 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [22 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [22 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [22 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [22 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack then use Alarm and current settings sheet within Matrix |  |  | VU11 |  |  |  | VU11 | [22 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) |  |  |  | VU10 |  |  |  | VU10 | [22 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) |  |  |  | VU9 |  |  |  | VU9 | [22 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [22 empty] | VU8 |  |  |  | VU8
Customer has decided to vary the initial maximum power capacity requirements so refer to job pack or APO order then use rectifier alarm and current limit settings sheet that has been included in the Matrix to find required settings. |  |  |  | VU7 |  |  |  | VU7 | [22 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [22 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [22 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [22 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [22 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [22 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [22 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | Front view | [5 empty] | Front view |  |  |  | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1 |  |  |  |  | RSU 2
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D |  |  |  |  | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4509
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [10 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4509
Power Base Cabinet Size | 600W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D | [5 empty] | Customer use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 10A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 10A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 6A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm | [5 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
[5 empty] | Power Base Cabinet | [5 empty] | Customer Use Cabinet in RSU
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8474
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8474
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC only - Standard System |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | Cabler riser for Customer cabling only | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x800D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4549
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [32 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4549
Power Base Cabinet Size | 600W x 800D (x2) |  |  | Standard superstructure assembly | [25 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [24 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only - Dual System
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [8 empty] | Customer Use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU3 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU4 600W x 800D |  | Power Base Cabinet 2 600W x 800D | [6 empty] | Power Base Cabinet 2 600W x 800D | [7 empty] | Customer Use Cabinet in RSU4 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU3 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  | L | Rear view |  | R |  | L | Rear view |  | R |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | AC Power Panel | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 4 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 4 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
The Broadcast Media orders are the first of their kind comprising of dual ac only Power Base Cabinets between which are 4 x CUC's. This means that we're looking for contiguous blocks of 6 cabinets side by side. |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Rear view |  |  |  |  | Rear view |  |  |  |  | Rear view |  |  |  |  | Front view | [5 empty] | Front View | [6 empty] | Rear view |  |  |  | Rear view |  |  |  |  | Rear view |  |  |  |  | Rear view |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  | 600mm | [6 empty] | 600mm | [7 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
[6 empty] | Rear | [25 empty] | Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2 |  |  |  |  | Customer Use Cabinet in RSU3 |  |  |  |  | Customer Use Cabinet in RSU4 | [5 empty] | Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [25 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [33 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7326
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [22 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7326
Power Base Cabinet Size | 600W x 800D (x2) |  |  | Standard superstructure assembly | [37 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only - Dual System
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [8 empty] | Customer Use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 800D |  | Power Base Cabinet 2 600W x 800D | [6 empty] | Power Base Cabinet 2 600W x 800D | [7 empty] | Customer Use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | AC Power Panel | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Rear view |  |  |  |  | Rear view | [5 empty] | Front View | [6 empty] | Rear view |  |  |  | Rear view |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm |  | 600mm | [6 empty] | 600mm | [7 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
[6 empty] | Rear | [15 empty] | Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2 | [5 empty] | Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [15 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [23 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5036
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [16 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5036
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [27 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Standard DC
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [8 empty] | Customer Use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 800D | [6 empty] | Customer Use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | Metered |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter provided |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Rear view |  |  |  |  | Rear view | [6 empty] | Rear view |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm | [6 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [17 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9180
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9180
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC + Std DC + inverter (750VA n+1) |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [7 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  | Cabler riser for Customer cabling only | VU48 |  | VU48
Expected future maximum power capacity | 2 |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [7 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x800D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0613
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [27 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0613
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [44 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [6 empty] | Customer Use Cabinet in RSU3 800W x 800D | [7 empty] | Customer Use Cabinet in RSU3 800W x 800D | [5 empty] | Customer Use Cabinet in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  |  | VU48 |  | VU48 |  |  |  | VU48 |  | VU48 |  |  |  | VU48 |  | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 10 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 3 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (to Molex FDU in CuC3) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [7 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU 2 | [6 empty] | Customer Use Cabinet on RSU 3
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0209
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [27 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0209
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [44 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [6 empty] | Customer Use Cabinet in RSU3 800W x 800D | [7 empty] | Customer Use Cabinet in RSU3 800W x 800D | [5 empty] | Customer Use Cabinet in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO Order / Job Pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 10 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 3 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (to Molex FDU in CuC3) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack then use Alarm and current settings sheet within Matrix |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [7 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU 2 | [6 empty] | Customer Use Cabinet on RSU 3
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1213
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [18 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1213
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [27 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer RSU2 (800W x 800D) | [5 empty] | Customer RSU2 (800W x 800D) |  |  |  | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | RSU2 800W x 800D x 2200H | [5 empty] | RSU2 800W x 800D x 2200H | [5 empty] | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 | [13 empty] | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 | [13 empty] | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 | [13 empty] | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 | [13 empty] | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 | [13 empty] | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 | [13 empty] | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 | [13 empty] | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 | [13 empty] | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | [13 empty] | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 | [13 empty] | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | [13 empty] | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 | [13 empty] | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 | [13 empty] | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 | [13 empty] | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 | [13 empty] | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 | [13 empty] | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 | [13 empty] | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 | [13 empty] | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 | [13 empty] | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 | [13 empty] | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 | [13 empty] | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 | [13 empty] | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 | [13 empty] | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 | [13 empty] | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 | [13 empty] | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 | [13 empty] | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 | [13 empty] | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 | [13 empty] | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 32A |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 | [13 empty] | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 6A |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | [13 empty] | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 6A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 | [13 empty] | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 | [13 empty] | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 | [13 empty] | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 | [13 empty] | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 | [13 empty] | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 | [13 empty] | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 | [13 empty] | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 | [13 empty] | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 | [13 empty] | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 | [13 empty] | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 | [13 empty] | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 | [13 empty] | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 | [13 empty] | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 | [13 empty] | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 | [13 empty] | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 | [13 empty] | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 | [13 empty] | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm | Front view | [5 empty] | Rear view |  |  |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm |  |  |  | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1 | [7 empty] | RSU2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9817
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [20 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9817
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [30 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 6 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9128
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9128
Power Base Cabinet Size | 600W x 600D (x2) |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Dual System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D |  |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View | [5 empty] | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
[5 empty] | Rear | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D | [5 empty] | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [5 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1768
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1768
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [18 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [9 empty] | Customer Use Cabinet in RSU1 600W x 800D | [6 empty] | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  |  |  | L | Rear view |  | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  | VU48 |  |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel |  |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU4
|  |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view | [6 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [9 empty] | 600mm | [6 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 | [5 empty] | Customer Use Cabinet in RSU1
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [13 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2234
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [16 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2234
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [25 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC + inverter (750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [6 empty] | Customer RSU1(600W x 600D) |  |  |  |  | Customer RSU2 (600W x 600D) | [5 empty] | Customer RSU2(600W x 600D) |  |  |  | Customer RSU1(600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 | [21 empty] | VU48 |  |  |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [21 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  |  | VU46 | [21 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [21 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 | [21 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [21 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [21 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [21 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [21 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [21 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  |  | VU38 | [21 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [21 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [21 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [21 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [21 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 | [21 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 | [21 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 | [21 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [21 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [21 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [21 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [21 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H | [5 empty] | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [21 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 | [21 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [21 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [21 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [21 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [21 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 | [21 empty] | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [21 empty] | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [21 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [21 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [21 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [21 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [21 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 | [21 empty] | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 | [21 empty] | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [21 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [21 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [21 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [21 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [21 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [21 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [21 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [21 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [21 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [21 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [6 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
[12 empty] | RSU 1 |  |  |  |  | RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D | [5 empty] | 600W x 600D |  |  |  |  | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8597
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8597
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [18 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [9 empty] | Customer Use Cabinet in RSU1 600W x 800D | [6 empty] | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | metered |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 1 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 2 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view | [6 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [9 empty] | 600mm | [6 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 | [5 empty] | Customer Use Cabinet in RSU1
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [13 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0259
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [10 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0259
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [15 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU1 (600W x 600D) | [5 empty] | Customer RSU1(600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [12 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [12 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 | [12 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [12 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [12 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [12 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter |  | VU42 | [12 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [12 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [12 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [12 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 | [12 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [12 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [12 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [12 empty] | VU35 |  | VU35
Openreach HDF option requirement | Customer will provide in own cabinet |  |  | VU34 |  |  | VU34 | [12 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [12 empty] | VU33 |  | VU33
Expected future maximum tie cables | 24 |  |  | VU32 |  |  | VU32 | [12 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [12 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [12 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [12 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [12 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [12 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [12 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [12 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [12 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [12 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [12 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [12 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [12 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [12 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [12 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [12 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [12 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [12 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [12 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [12 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [12 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [12 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [12 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [12 empty] | VU8 |  | VU8
MDF ties to be terminated in the customer provided cabinet |  |  |  | VU7 |  |  | VU7 | [12 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [12 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [12 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [12 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [12 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [12 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [12 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm | [5 empty] | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0772
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [15 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0772
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [24 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC +inverter (750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [5 empty] | Customer RSU1 (600W x 800D) |  |  |  |  | Customer RSU2 (600W x 800D) | [5 empty] | Customer RSU2(600W x 800D) |  |  |  | Customer RSU1(600W x 800D) |  |  |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [21 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [21 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 | [21 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [21 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [21 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [21 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [21 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [21 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [21 empty] | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 | [21 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 | [21 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [21 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [21 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [21 empty] | VU35 |  | VU35
Openreach HDF option requirement | Customer will provide in own cabinet |  |  | VU34 |  |  | VU34 | [21 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [21 empty] | VU33 |  | VU33
Expected future maximum tie cables | 20 |  |  | VU32 |  |  | VU32 | [21 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [21 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [21 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [21 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [21 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [21 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 800D x 2200H |  |  |  |  | RSU2 600W x 800D x 2200H | [5 empty] | RSU2 600W x 800D x 2200H |  |  |  | RSU1 600W x 800D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [21 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [21 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [21 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [21 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [21 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [21 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [21 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [21 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [21 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [21 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [21 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [21 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [21 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [21 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [21 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [21 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [21 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [21 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [21 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [21 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [21 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [21 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [21 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [21 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [21 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm | [7 empty] | 600mm |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
[11 empty] | RSU 1 |  |  |  |  | RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3468
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [11 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3468
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only - Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [9 empty] | Customer use Cabinet in RSU 600W x 800D | [5 empty] | Customer use Cabinet in RSU 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU4
|  |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View | [5 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [9 empty] | 600mm | [5 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post) | [11 empty] | Customer Use Cabinet in RSU
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4750
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [16 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4750
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [25 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC +inverter (750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Customer RSU1 (600W x 800D) |  |  |  |  | Customer RSU2 (600W x 800D) | [5 empty] | Customer RSU2(600W x 800D) |  |  |  | Customer RSU1(600W x 800D) |  |  |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 | [21 empty] | VU48 |  |  |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [21 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 | [21 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [21 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 | [21 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [21 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [21 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [21 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [21 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 | [21 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  |  | VU38 | [21 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [21 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [21 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [21 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [21 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 | [21 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 | [21 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 | [21 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [21 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [21 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [21 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [21 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  | RSU1 600W x 800D x 2200H |  |  |  |  | RSU2 600W x 800D x 2200H | [5 empty] | RSU2 600W x 800D x 2200H |  |  |  | RSU1 600W x 800D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [21 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 | [21 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [21 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [21 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [21 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [21 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 | [21 empty] | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [21 empty] | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [21 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [21 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [21 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [21 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [21 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 | [21 empty] | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 | [21 empty] | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [21 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [21 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [21 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [21 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [21 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [21 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [21 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [21 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [21 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [21 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [6 empty] | 600mm | [7 empty] | 600mm |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
[12 empty] | RSU 1 |  |  |  |  | RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9674
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [11 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9674
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1) |  |  |  |  | Standard superstructure assembly | [14 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer RSU (800W x 800D) | [5 empty] | Customer RSU (800W x 800D) |  |  |  | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only | RSU1 800W x 800D x 2200H | [5 empty] | RSU1 800W x 800D x 2200H |  |  |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [13 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  | VU46 | [13 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 | [13 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [13 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [13 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [13 empty] | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 | [13 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 | [13 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [13 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [13 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [13 empty] | VU35 |  | VU35
Openreach HDF option requirement | Customer will provide in own cabinet |  |  | VU34 |  |  | VU34 | [13 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [13 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [13 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [13 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [13 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [13 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [13 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [13 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 | [13 empty] | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [13 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [13 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [13 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [13 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [13 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [13 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [13 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [13 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [13 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [13 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [13 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [13 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [13 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 | [13 empty] | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [13 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [13 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [13 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [13 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [13 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [13 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [13 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [13 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [13 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [13 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm | Front view | [5 empty] | Rear view |  |  |  |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [5 empty] | 800mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [5 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 | [5 empty] | RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D
[6 empty] | Front | [5 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5605
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [11 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5605
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [8 empty] | Customer Use Cabinet in RSU1 600W x 800D | [6 empty] | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 | AC PDU & Flex tie bar |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 2 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Rear view | [6 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm | [6 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet in RSU1
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [12 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2059
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2059
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | AC Power Panel | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8230
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [43 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8230
Power Base Cabinet Size | 600W x 800D (x2) |  |  | Standard superstructure assembly | [35 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [30 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 800D | [5 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Power Base Cabinet #2 600W x 800D | [5 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | HDF Cabinet 800W x 800D | [6 empty] | HDF Cabinet 800W x 800D |  |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #2 600W x 800D |  |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #1 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [12 empty] | VU48 |  |  | VU48 | [16 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  | VU48 | [15 empty] | VU48 |  | VU48 | [10 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [12 empty] | VU47 |  |  | VU47 | [16 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47 | [15 empty] | VU47 |  | VU47 | [10 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [12 empty] | VU46 |  |  | VU46 | [16 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46 | [15 empty] | VU46 |  | VU46 | [10 empty] | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 | [12 empty] | VU45 | DC Power System Chassis |  | VU45 | [16 empty] | VU45 |  |  |  | VU45 |  |  | VU45 |  | VU45 | [15 empty] | VU45 | AC Power Panel & Meter | VU45 | [10 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [12 empty] | VU44 |  |  | VU44 | [16 empty] | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44 | [15 empty] | VU44 |  | VU44 | [10 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [12 empty] | VU43 |  |  | VU43 | [16 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43 | [15 empty] | VU43 |  | VU43 | [10 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter provided |  | VU42 | [12 empty] | VU42 | Nil Modules provided |  | VU42 | [16 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42 | [15 empty] | VU42 |  | VU42 | [10 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [12 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [16 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  | VU41 | [15 empty] | VU41 | AC PDU & Flex tie bar | VU41 | [10 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [12 empty] | VU40 |  |  | VU40 | [16 empty] | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40 | [15 empty] | VU40 |  | VU40 | [10 empty] | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 | [12 empty] | VU39 |  |  | VU39 | [16 empty] | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39 | [15 empty] | VU39 |  | VU39 | [10 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 5 |  |  | VU38 |  |  | VU38 | [12 empty] | VU38 |  |  | VU38 | [16 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38 | [15 empty] | VU38 |  | VU38 | [10 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [12 empty] | VU37 |  |  | VU37 | [16 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37 | [15 empty] | VU37 |  | VU37 | [10 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [12 empty] | VU36 |  |  | VU36 | [16 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36 | [15 empty] | VU36 |  | VU36 | [10 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [12 empty] | VU35 |  |  | VU35 | [16 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 |  | VU35 | [15 empty] | VU35 |  | VU35 | [10 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [12 empty] | VU34 |  |  | VU34 | [16 empty] | VU34 | MDF Tie # 19 | MDF Tie # 21 | MDF Tie # 22 | VU34 |  |  | VU34 |  | VU34 | [15 empty] | VU34 |  | VU34 | [10 empty] | VU34 |  | VU34
HDF Sub racks provided | 7 |  |  | VU33 |  |  | VU33 | [12 empty] | VU33 |  |  | VU33 | [16 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33 | [15 empty] | VU33 |  | VU33 | [10 empty] | VU33 |  | VU33
Expected future maximum tie cables | 19 |  |  | VU32 |  |  | VU32 | [12 empty] | VU32 |  |  | VU32 | [16 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32 | [15 empty] | VU32 |  | VU32 | [10 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [12 empty] | VU31 |  |  | VU31 | [16 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31 | [15 empty] | VU31 |  | VU31 | [10 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [12 empty] | VU30 |  |  | VU30 | [16 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 |  | VU30 | [15 empty] | VU30 |  | VU30 | [10 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [12 empty] | VU29 |  |  | VU29 | [16 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 |  | VU29 | [15 empty] | VU29 |  | VU29 | [10 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [12 empty] | VU28 |  |  | VU28 | [16 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28 | [15 empty] | VU28 |  | VU28 | [10 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [12 empty] | VU27 |  |  | VU27 | [16 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27 | [15 empty] | VU27 |  | VU27 | [10 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 800D x 2200H |  |  |  |  | RSU2 600W x 800D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | RSU3 600W x 800D x 2200H |  |  |  |  | RSU4 600W x 800D x 2200H |  |  |  |  | RSU5 600W x 800D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26 |  |  |  | RSU5 600W x 800D x 2200H |  |  |  | RSU4 600W x 800D x 2200H |  |  |  | RSU3 600W x 800D x 2200H |  |  |  | VU26 |  | VU26 |  |  | RSU2 600W x 800D x 2200H |  |  |  | RSU1 600W x 800D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [12 empty] | VU25 |  |  | VU25 | [16 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 |  | VU25 | [15 empty] | VU25 |  | VU25 | [10 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [12 empty] | VU24 |  |  | VU24 | [16 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 |  | VU24 | [15 empty] | VU24 |  | VU24 | [10 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [12 empty] | VU23 |  |  | VU23 | [16 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23 | [15 empty] | VU23 |  | VU23 | [10 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [12 empty] | VU22 |  |  | VU22 | [16 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22 | [15 empty] | VU22 |  | VU22 | [10 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [12 empty] | VU21 |  |  | VU21 | [16 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21 | [15 empty] | VU21 |  | VU21 | [10 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [12 empty] | VU20 |  |  | VU20 | [16 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 |  | VU20 | [15 empty] | VU20 |  | VU20 | [10 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [12 empty] | VU19 |  |  | VU19 | [16 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 |  | VU19 | [15 empty] | VU19 |  | VU19 | [10 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [12 empty] | VU18 |  |  | VU18 | [16 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18 | [15 empty] | VU18 |  | VU18 | [10 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A(default) |  |  | VU17 |  |  | VU17 | [12 empty] | VU17 |  |  | VU17 | [16 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17 | [15 empty] | VU17 |  | VU17 | [10 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A(default) |  |  | VU16 |  |  | VU16 | [12 empty] | VU16 |  |  | VU16 | [16 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16 | [15 empty] | VU16 |  | VU16 | [10 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A(default) |  |  | VU15 |  |  | VU15 | [12 empty] | VU15 |  |  | VU15 | [16 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 |  | VU15 | [15 empty] | VU15 |  | VU15 | [10 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [12 empty] | VU14 |  |  | VU14 | [16 empty] | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 |  |  | VU14 |  | VU14 | [15 empty] | VU14 |  | VU14 | [10 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [12 empty] | VU13 |  |  | VU13 | [16 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13 | [15 empty] | VU13 |  | VU13 | [10 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [12 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [16 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  | VU12 | [15 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [10 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [12 empty] | VU11 |  |  | VU11 | [16 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11 | [15 empty] | VU11 |  | VU11 | [10 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [12 empty] | VU10 |  |  | VU10 | [16 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 |  | VU10 | [15 empty] | VU10 |  | VU10 | [10 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [12 empty] | VU9 |  |  | VU9 | [16 empty] | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 |  | VU9 | [15 empty] | VU9 |  | VU9 | [10 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [12 empty] | VU8 |  |  | VU8 | [16 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8 | [15 empty] | VU8 |  | VU8 | [10 empty] | VU8 |  | VU8
Customer has requested that tie cables are terminated on the front of the HDF only and numbered from left to right. |  |  |  | VU7 |  |  | VU7 | [12 empty] | VU7 |  |  | VU7 | [16 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7 | [15 empty] | VU7 |  | VU7 | [10 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [12 empty] | VU6 |  |  | VU6 | [16 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6 | [15 empty] | VU6 |  | VU6 | [10 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [12 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [16 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 |  | VU5 | [15 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [10 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [12 empty] | VU4 |  |  | VU4 | [16 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 |  | VU4 | [15 empty] | VU4 |  | VU4 | [10 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [12 empty] | VU3 |  |  | VU3 | [16 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3 | [15 empty] | VU3 |  | VU3 | [10 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [12 empty] | VU2 |  |  | VU2 | [16 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2 | [15 empty] | VU2 |  | VU2 | [10 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [12 empty] | VU1 |  |  | VU1 | [16 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1 | [15 empty] | VU1 |  | VU1 | [10 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[5 empty] | Power Base Cabinet #1 | [16 empty] | Power Base Cabinet #2 | [18 empty] | HDF Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 | [10 empty] | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 800W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [15 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5979
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [43 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5979
Power Base Cabinet Size | 600W x 800D (x2) |  |  | Standard superstructure assembly | [35 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [30 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+inverter (750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 800D | [5 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Power Base Cabinet #2 600W x 800D | [5 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | HDF Cabinet 800W x 800D | [6 empty] | HDF Cabinet 800W x 800D |  |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #2 600W x 800D |  |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #1 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [12 empty] | VU48 |  |  | VU48 | [16 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  | VU48 | [15 empty] | VU48 |  | VU48 | [10 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [12 empty] | VU47 |  |  | VU47 | [16 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47 | [15 empty] | VU47 |  | VU47 | [10 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [12 empty] | VU46 |  |  | VU46 | [16 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46 | [15 empty] | VU46 |  | VU46 | [10 empty] | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 | [12 empty] | VU45 | DC Power System Chassis |  | VU45 | [16 empty] | VU45 |  |  |  | VU45 |  |  | VU45 |  | VU45 | [15 empty] | VU45 | AC Power Panel & Meter | VU45 | [10 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [12 empty] | VU44 |  |  | VU44 | [16 empty] | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44 | [15 empty] | VU44 |  | VU44 | [10 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [12 empty] | VU43 |  |  | VU43 | [16 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43 | [15 empty] | VU43 |  | VU43 | [10 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [12 empty] | VU42 | Inverter Chassis |  | VU42 | [16 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42 | [15 empty] | VU42 |  | VU42 | [10 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [12 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [16 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  | VU41 | [15 empty] | VU41 | AC PDU & Flex tie bar | VU41 | [10 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [12 empty] | VU40 |  |  | VU40 | [16 empty] | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40 | [15 empty] | VU40 |  | VU40 | [10 empty] | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 | [12 empty] | VU39 |  |  | VU39 | [16 empty] | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39 | [15 empty] | VU39 |  | VU39 | [10 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 5 |  |  | VU38 |  |  | VU38 | [12 empty] | VU38 |  |  | VU38 | [16 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38 | [15 empty] | VU38 |  | VU38 | [10 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [12 empty] | VU37 |  |  | VU37 | [16 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37 | [15 empty] | VU37 |  | VU37 | [10 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [12 empty] | VU36 |  |  | VU36 | [16 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36 | [15 empty] | VU36 |  | VU36 | [10 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [12 empty] | VU35 |  |  | VU35 | [16 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 |  | VU35 | [15 empty] | VU35 |  | VU35 | [10 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [12 empty] | VU34 |  |  | VU34 | [16 empty] | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 |  |  | VU34 |  | VU34 | [15 empty] | VU34 |  | VU34 | [10 empty] | VU34 |  | VU34
HDF Sub racks provided | 7 |  |  | VU33 |  |  | VU33 | [12 empty] | VU33 |  |  | VU33 | [16 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33 | [15 empty] | VU33 |  | VU33 | [10 empty] | VU33 |  | VU33
Expected future maximum tie cables | 19 |  |  | VU32 |  |  | VU32 | [12 empty] | VU32 |  |  | VU32 | [16 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32 | [15 empty] | VU32 |  | VU32 | [10 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [12 empty] | VU31 |  |  | VU31 | [16 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31 | [15 empty] | VU31 |  | VU31 | [10 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [12 empty] | VU30 |  |  | VU30 | [16 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 |  | VU30 | [15 empty] | VU30 |  | VU30 | [10 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [12 empty] | VU29 |  |  | VU29 | [16 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 |  | VU29 | [15 empty] | VU29 |  | VU29 | [10 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [12 empty] | VU28 |  |  | VU28 | [16 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28 | [15 empty] | VU28 |  | VU28 | [10 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [12 empty] | VU27 |  |  | VU27 | [16 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27 | [15 empty] | VU27 |  | VU27 | [10 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 800D x 2200H |  |  |  |  | RSU2 600W x 800D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | RSU3 600W x 800D x 2200H |  |  |  |  | RSU4 600W x 800D x 2200H |  |  |  |  | RSU5 600W x 800D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26 |  |  |  | RSU5 600W x 800D x 2200H |  |  |  | RSU4 600W x 800D x 2200H |  |  |  | RSU3 600W x 800D x 2200H |  |  |  | VU26 |  | VU26 |  |  | RSU2 600W x 800D x 2200H |  |  |  | RSU1 600W x 800D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [12 empty] | VU25 |  |  | VU25 | [16 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 |  | VU25 | [15 empty] | VU25 |  | VU25 | [10 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [12 empty] | VU24 |  |  | VU24 | [16 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 |  | VU24 | [15 empty] | VU24 |  | VU24 | [10 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [12 empty] | VU23 |  |  | VU23 | [16 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23 | [15 empty] | VU23 |  | VU23 | [10 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [12 empty] | VU22 |  |  | VU22 | [16 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22 | [15 empty] | VU22 |  | VU22 | [10 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [12 empty] | VU21 |  |  | VU21 | [16 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21 | [15 empty] | VU21 |  | VU21 | [10 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [12 empty] | VU20 |  |  | VU20 | [16 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 |  | VU20 | [15 empty] | VU20 |  | VU20 | [10 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [12 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [16 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 |  | VU19 | [15 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19 | [10 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [12 empty] | VU18 |  |  | VU18 | [16 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18 | [15 empty] | VU18 |  | VU18 | [10 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [12 empty] | VU17 |  |  | VU17 | [16 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17 | [15 empty] | VU17 |  | VU17 | [10 empty] | VU17 |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  | VU16 | [12 empty] | VU16 |  |  | VU16 | [16 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16 | [15 empty] | VU16 |  | VU16 | [10 empty] | VU16 |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  | VU15 | [12 empty] | VU15 |  |  | VU15 | [16 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 |  | VU15 | [15 empty] | VU15 |  | VU15 | [10 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [12 empty] | VU14 |  |  | VU14 | [16 empty] | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 |  |  | VU14 |  | VU14 | [15 empty] | VU14 |  | VU14 | [10 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [12 empty] | VU13 |  |  | VU13 | [16 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13 | [15 empty] | VU13 |  | VU13 | [10 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [12 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [16 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  | VU12 | [15 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [10 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [12 empty] | VU11 |  |  | VU11 | [16 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11 | [15 empty] | VU11 |  | VU11 | [10 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [12 empty] | VU10 |  |  | VU10 | [16 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 |  | VU10 | [15 empty] | VU10 |  | VU10 | [10 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [12 empty] | VU9 |  |  | VU9 | [16 empty] | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 |  | VU9 | [15 empty] | VU9 |  | VU9 | [10 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [12 empty] | VU8 |  |  | VU8 | [16 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8 | [15 empty] | VU8 |  | VU8 | [10 empty] | VU8 |  | VU8
HDF Sub rack configuration and MDF tie cable numbering has been modified to reflect customers specific instructions |  |  |  | VU7 |  |  | VU7 | [12 empty] | VU7 |  |  | VU7 | [16 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7 | [15 empty] | VU7 |  | VU7 | [10 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [12 empty] | VU6 |  |  | VU6 | [16 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6 | [15 empty] | VU6 |  | VU6 | [10 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [12 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [16 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 |  | VU5 | [15 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [10 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [12 empty] | VU4 |  |  | VU4 | [16 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie #3 | VU4 |  |  | VU4 |  | VU4 | [15 empty] | VU4 |  | VU4 | [10 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [12 empty] | VU3 |  |  | VU3 | [16 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3 | [15 empty] | VU3 |  | VU3 | [10 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [12 empty] | VU2 |  |  | VU2 | [16 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2 | [15 empty] | VU2 |  | VU2 | [10 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [12 empty] | VU1 |  |  | VU1 | [16 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1 | [15 empty] | VU1 |  | VU1 | [10 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[5 empty] | Power Base Cabinet #1 | [16 empty] | Power Base Cabinet #2 | [18 empty] | HDF Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 | [10 empty] | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 800W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [15 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3912
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3912
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 3 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 7 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [13 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [13 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 3 |  |  | VU24 | [13 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU23 | [13 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [13 empty] | VU19 | HDF Sub rack # 2 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [13 empty] | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [13 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [13 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [13 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1422
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1422
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 2.0 kw |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | OR EAD & OSA Router(1 x AC each) |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 | OR 1U EAD 100/1000 (2 x DC Molex) |  |  | VU38 | [13 empty] | VU38 | GEA Brush Panel |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fibre Tray |  |  | VU37 | [13 empty] | VU37 | GEA Brush Panel |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 | Customer Equipment |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 4 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 12 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 | Customer Equipment |  |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 | OR EAD 10Gbps / VM TM102 10 Gbps (2 x DC Molex) |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [13 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [13 empty] | VU28 | Customer Equipment |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 | Space reserved for HDF Sub Rack # 6 |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  | Customer Equipment |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | OR EAD Multi Slot Chassis 100/1000 (2 x DC Molex) |  |  | VU24 | [13 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [13 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 | Space reserved for HDF Sub Rack # 5 |  |  | VU22
Ways 1 & 9 | 20A |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 | [13 empty] | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [13 empty] | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 | HDF Sub rack # 3 |  |  | VU17 | [13 empty] | VU17 | HDF Sub rack # 4 |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU16 | [13 empty] | VU16 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 | [13 empty] | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 | [13 empty] | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4284
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [20 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4284
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [30 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 5 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4770
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [21 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4770
Power Base Cabinet Size | 600W x 800D (x2) |  |  | Standard superstructure assembly | [34 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 800D | [5 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Power Base Cabinet #2 600W x 800D | [5 empty] | Power Base Cabinet #2 600W x 800D |  |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #1 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [12 empty] | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 | [10 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [12 empty] | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 | [10 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [12 empty] | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 | [10 empty] | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 | [12 empty] | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45 | [10 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [12 empty] | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 | [10 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [12 empty] | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 | [10 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter provided |  | VU42 | [12 empty] | VU42 | Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42 | [10 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [12 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41 | [10 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [12 empty] | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 | [10 empty] | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 | [12 empty] | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 | [10 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 | [12 empty] | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 | [10 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [12 empty] | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 | [10 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [12 empty] | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 | [10 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [12 empty] | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 | [10 empty] | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [12 empty] | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 | [10 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [12 empty] | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 | [10 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [12 empty] | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 | [10 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [12 empty] | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 | [10 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [12 empty] | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 | [10 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [12 empty] | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 | [10 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [12 empty] | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 | [10 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [12 empty] | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 | [10 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 800D x 2200H |  |  |  |  | RSU2 600W x 800D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | RSU2 600W x 800D x 2200H |  |  |  | RSU1 600W x 800D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [12 empty] | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 | [10 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [12 empty] | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 | [10 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [12 empty] | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 | [10 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [12 empty] | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 | [10 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [12 empty] | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 | [10 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [12 empty] | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 | [10 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [12 empty] | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 | [10 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [12 empty] | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 | [10 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [12 empty] | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 | [10 empty] | VU17 |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  | VU16 | [12 empty] | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 | [10 empty] | VU16 |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  | VU15 | [12 empty] | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 | [10 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [12 empty] | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 | [10 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [12 empty] | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 | [10 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [12 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [10 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [12 empty] | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 | [10 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [12 empty] | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 | [10 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [12 empty] | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 | [10 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [12 empty] | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 | [10 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [12 empty] | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 | [10 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [12 empty] | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 | [10 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [12 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [10 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [12 empty] | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 | [10 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [12 empty] | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 | [10 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [12 empty] | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 | [10 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [12 empty] | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 | [10 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Front View | [5 empty] | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[5 empty] | Power Base Cabinet #1 | [16 empty] | Power Base Cabinet #2
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [15 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7805
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [43 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7805
Power Base Cabinet Size | 600W x 600D (x2) |  |  | Standard superstructure assembly | [15 empty] | Standard superstructure assembly | [19 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [17 empty] | Standard superstructure assembly | [12 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Power Base Cabinet #2 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Power Base Cabinet #2 600W x 600D |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [12 empty] | VU48 |  |  | VU48 | [16 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  | VU48 | [15 empty] | VU48 |  | VU48 | [10 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [12 empty] | VU47 |  |  | VU47 | [16 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47 | [15 empty] | VU47 |  | VU47 | [10 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [12 empty] | VU46 |  |  | VU46 | [16 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46 | [15 empty] | VU46 |  | VU46 | [10 empty] | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 | [12 empty] | VU45 | DC Power System Chassis |  | VU45 | [16 empty] | VU45 |  |  |  | VU45 |  |  | VU45 |  | VU45 | [15 empty] | VU45 | AC Power Panel & Meter | VU45 | [10 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [12 empty] | VU44 |  |  | VU44 | [16 empty] | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44 | [15 empty] | VU44 |  | VU44 | [10 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules)per Power Base cabinet | 0 |  |  | VU43 |  |  | VU43 | [12 empty] | VU43 |  |  | VU43 | [16 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43 | [15 empty] | VU43 |  | VU43 | [10 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 0 |  |  | VU42 | Nil Inverter |  | VU42 | [12 empty] | VU42 | Nil Inverter |  | VU42 | [16 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42 | [15 empty] | VU42 |  | VU42 | [10 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [12 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [16 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  | VU41 | [15 empty] | VU41 | AC PDU & Flex tie bar | VU41 | [10 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [12 empty] | VU40 |  |  | VU40 | [16 empty] | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40 | [15 empty] | VU40 |  | VU40 | [10 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [12 empty] | VU39 |  |  | VU39 | [16 empty] | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39 | [15 empty] | VU39 |  | VU39 | [10 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 5 |  |  | VU38 |  |  | VU38 | [12 empty] | VU38 |  |  | VU38 | [16 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38 | [15 empty] | VU38 |  | VU38 | [10 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [12 empty] | VU37 |  |  | VU37 | [16 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37 | [15 empty] | VU37 |  | VU37 | [10 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [12 empty] | VU36 |  |  | VU36 | [16 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36 | [15 empty] | VU36 |  | VU36 | [10 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [12 empty] | VU35 |  |  | VU35 | [16 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 |  | VU35 | [15 empty] | VU35 |  | VU35 | [10 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [12 empty] | VU34 |  |  | VU34 | [16 empty] | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 |  |  | VU34 |  | VU34 | [15 empty] | VU34 |  | VU34 | [10 empty] | VU34 |  | VU34
HDF Sub racks provided | 7 |  |  | VU33 |  |  | VU33 | [12 empty] | VU33 |  |  | VU33 | [16 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33 | [15 empty] | VU33 |  | VU33 | [10 empty] | VU33 |  | VU33
Expected future maximum tie cables | 19 |  |  | VU32 |  |  | VU32 | [12 empty] | VU32 |  |  | VU32 | [16 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32 | [15 empty] | VU32 |  | VU32 | [10 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [12 empty] | VU31 |  |  | VU31 | [16 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31 | [15 empty] | VU31 |  | VU31 | [10 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [12 empty] | VU30 |  |  | VU30 | [16 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 |  | VU30 | [15 empty] | VU30 |  | VU30 | [10 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [12 empty] | VU29 |  |  | VU29 | [16 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 |  | VU29 | [15 empty] | VU29 |  | VU29 | [10 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [12 empty] | VU28 |  |  | VU28 | [16 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28 | [15 empty] | VU28 |  | VU28 | [10 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [12 empty] | VU27 |  |  | VU27 | [16 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27 | [15 empty] | VU27 |  | VU27 | [10 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26 |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | VU26 |  | VU26 |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [12 empty] | VU25 |  |  | VU25 | [16 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 |  | VU25 | [15 empty] | VU25 |  | VU25 | [10 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [12 empty] | VU24 |  |  | VU24 | [16 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 |  | VU24 | [15 empty] | VU24 |  | VU24 | [10 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [12 empty] | VU23 |  |  | VU23 | [16 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23 | [15 empty] | VU23 |  | VU23 | [10 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [12 empty] | VU22 |  |  | VU22 | [16 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22 | [15 empty] | VU22 |  | VU22 | [10 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [12 empty] | VU21 |  |  | VU21 | [16 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21 | [15 empty] | VU21 |  | VU21 | [10 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [12 empty] | VU20 |  |  | VU20 | [16 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 |  | VU20 | [15 empty] | VU20 |  | VU20 | [10 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [12 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [16 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 |  | VU19 | [15 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19 | [10 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [12 empty] | VU18 |  |  | VU18 | [16 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18 | [15 empty] | VU18 |  | VU18 | [10 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [12 empty] | VU17 |  |  | VU17 | [16 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17 | [15 empty] | VU17 |  | VU17 | [10 empty] | VU17 |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  | VU16 | [12 empty] | VU16 |  |  | VU16 | [16 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16 | [15 empty] | VU16 |  | VU16 | [10 empty] | VU16 |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  | VU15 | [12 empty] | VU15 |  |  | VU15 | [16 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 |  | VU15 | [15 empty] | VU15 |  | VU15 | [10 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [12 empty] | VU14 |  |  | VU14 | [16 empty] | VU14 | MDF Tie #7 | MDF Tie # 8 | MDF Tie #9 | VU14 |  |  | VU14 |  | VU14 | [15 empty] | VU14 |  | VU14 | [10 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [12 empty] | VU13 |  |  | VU13 | [16 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13 | [15 empty] | VU13 |  | VU13 | [10 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [12 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [16 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  | VU12 | [15 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [10 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [12 empty] | VU11 |  |  | VU11 | [16 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11 | [15 empty] | VU11 |  | VU11 | [10 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [12 empty] | VU10 |  |  | VU10 | [16 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 |  | VU10 | [15 empty] | VU10 |  | VU10 | [10 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [12 empty] | VU9 |  |  | VU9 | [16 empty] | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 |  | VU9 | [15 empty] | VU9 |  | VU9 | [10 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [12 empty] | VU8 |  |  | VU8 | [16 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8 | [15 empty] | VU8 |  | VU8 | [10 empty] | VU8 |  | VU8
The customer has requested that the MDF tie cables are terminated on the front of the HDF from the bottom upwards and numbered from left to right |  |  |  | VU7 |  |  | VU7 | [12 empty] | VU7 |  |  | VU7 | [16 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7 | [15 empty] | VU7 |  | VU7 | [10 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [12 empty] | VU6 |  |  | VU6 | [16 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6 | [15 empty] | VU6 |  | VU6 | [10 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [12 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [16 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 |  | VU5 | [15 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [10 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [12 empty] | VU4 |  |  | VU4 | [16 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie #3 | VU4 |  |  | VU4 |  | VU4 | [15 empty] | VU4 |  | VU4 | [10 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [12 empty] | VU3 |  |  | VU3 | [16 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3 | [15 empty] | VU3 |  | VU3 | [10 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [12 empty] | VU2 |  |  | VU2 | [16 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2 | [15 empty] | VU2 |  | VU2 | [10 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [12 empty] | VU1 |  |  | VU1 | [16 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1 | [15 empty] | VU1 |  | VU1 | [10 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1 | [16 empty] | Power Base Cabinet #2 | [19 empty] | HDF Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 | [10 empty] | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D | [5 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [15 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8201
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [47 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8201
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [39 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [35 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC +Inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | 10 |  |  | VU48 |  |  | VU48 | [36 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [31 empty] | VU48 |  | VU48
Expected future maximum power capacity | 10 |  |  | VU47 |  |  | VU47 | [36 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [31 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [36 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [31 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [36 empty] | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | [31 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 | [36 empty] | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 | [31 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [36 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [31 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [36 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [31 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [36 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [31 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [36 empty] | VU40 | HDF Sub rack # 15 |  |  | VU40 |  |  | VU40 | HDF Sub rack # 16 |  |  | VU40 | [31 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [36 empty] | VU39 | MDF Tie # 45 | MDF Tie # 44 | MDF Tie # 43 | VU39 |  |  | VU39 | MDF Tie # 46 | MDF Tie # 47 | MDF Tie # 48 | VU39 | [31 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 7 |  |  | VU38 |  |  | VU38 | [36 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [31 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [36 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [31 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [36 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [31 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [36 empty] | VU35 | HDF Sub rack # 13 |  |  | VU35 |  |  | VU35 | HDF Sub rack # 14 |  |  | VU35 | [31 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [36 empty] | VU34 | MDF Tie # 39 | MDF Tie # 38 | MDF Tie # 37 | VU34 |  |  | VU34 | MDF Tie # 40 | MDF Tie # 41 | MDF Tie # 42 | VU34 | [31 empty] | VU34 |  | VU34
HDF Sub racks provided | 16 |  |  | VU33 |  |  | VU33 | [36 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [31 empty] | VU33 |  | VU33
Expected future maximum tie cables | 48 |  |  | VU32 |  |  | VU32 | [36 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [31 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [36 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [31 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [36 empty] | VU30 | HDF Sub rack # 11 |  |  | VU30 |  |  | VU30 | HDF Sub rack # 12 |  |  | VU30 | [31 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [36 empty] | VU29 | MDF Tie # 33 | MDF Tie # 32 | MDF Tie # 31 | VU29 |  |  | VU29 | MDF Tie # 34 | MDF Tie # 35 | MDF Tie # 36 | VU29 | [31 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [36 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [31 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [36 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [31 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  |  | RSU5 600W x 600D x 2200H |  |  |  |  | RSU6 600W x 600D x 2200H |  |  |  |  | RSU7 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU7 600W x 600D x 2200H |  |  |  | RSU6 600W x 600D x 2200H |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [36 empty] | VU25 | HDF Sub rack # 9 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 10 |  |  | VU25 | [31 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [36 empty] | VU24 | MDF Tie # 27 | MDF Tie # 26 | MDF Tie # 25 | VU24 |  |  | VU24 | MDF Tie # 28 | MDF Tie # 29 | MDF Tie # 30 | VU24 | [31 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [36 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [31 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [36 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [31 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [36 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [31 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [36 empty] | VU20 | HDF Sub rack # 7 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 8 |  |  | VU20 | [31 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [36 empty] | VU19 | MDF Tie # 21 | MDF Tie # 20 | MDF Tie # 19 | VU19 |  |  | VU19 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU19 | [31 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [36 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [31 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [36 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [31 empty] | VU17 |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  | VU16 | [36 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [31 empty] | VU16 |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  | VU15 | [36 empty] | VU15 | HDF Sub rack # 5 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 6 |  |  | VU15 | [31 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [36 empty] | VU14 | MDF Tie # 15 | MDF Tie # 14 | MDF Tie #13 | VU14 |  |  | VU14 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie #18 | VU14 | [31 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [36 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [31 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [36 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [31 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | 174.3 |  |  | VU11 |  |  | VU11 | [36 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [31 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | 156.9 |  |  | VU10 |  |  | VU10 | [36 empty] | VU10 | HDF Sub rack # 3 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 4 |  |  | VU10 | [31 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | 191.7 |  |  | VU9 |  |  | VU9 | [36 empty] | VU9 | MDF Tie # 9 | MDF Tie # 8 | MDF Tie # 7 | VU9 |  |  | VU9 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU9 | [31 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [36 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [31 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [36 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [31 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [36 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [31 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [36 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5 | [31 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [36 empty] | VU4 | MDF Tie # 3 | MDF Tie # 2 | MDF Tie #1 | VU4 |  |  | VU4 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU4 | [31 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [36 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [31 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [36 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [31 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [36 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [31 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1 | [40 empty] | HDF Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | RSU6 |  |  |  |  | RSU7 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9591
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [15 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9591
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [24 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC + inverter (750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU1(600W x 600D) |  |  |  |  | Customer RSU2 (600W x 600D) | [5 empty] | Customer RSU2(600W x 600D) |  |  |  | Customer RSU1(600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [21 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [21 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 | [21 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [21 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [21 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [21 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [21 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [21 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [21 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [21 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 | [21 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [21 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [21 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [21 empty] | VU35 |  | VU35
Openreach HDF option requirement | Customer will provide in own cabinet |  |  | VU34 |  |  | VU34 | [21 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [21 empty] | VU33 |  | VU33
Expected future maximum tie cables | 20 |  |  | VU32 |  |  | VU32 | [21 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [21 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [21 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [21 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [21 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [21 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H | [5 empty] | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [21 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [21 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [21 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [21 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [21 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [21 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [21 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [21 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [21 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [21 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [21 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [21 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [21 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [21 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [21 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [21 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [21 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [21 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [21 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [21 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [21 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [21 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [21 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [21 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [21 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
[11 empty] | RSU 1 |  |  |  |  | RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0666
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [15 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0666
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [26 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU2 600W x 800D | [5 empty] | Customer use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil inverter provided |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CUC 2) |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CUC 1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9721
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [15 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9721
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [26 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + EBC DC
Standby AC power | Deploy when Non-ESS | Power Base Cabinet 600W x 800D | [8 empty] | EBC-C#1 of 1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU1 600W x 800D | [5 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | EBC-C#1 of 1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | EBC-C battery breaker switchgear |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 | 16-Way Molex DC sub-distribution module |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil inverter provided |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 2 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 2 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  | VU19 | BATTERY ENCLOSURE #6 - (all access from front) |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 | BATTERY ENCLOSURE #6 - (all access from front) |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in EBC 1 ) |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CUC 1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 | BATTERY ENCLOSURE #5 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 | BATTERY ENCLOSURE #5 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Build requires EBC cabinet 600Wx800D to accommodate the additional batteries in lieu of ESS power |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 | BATTERY ENCLOSURE #4 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 | BATTERY ENCLOSURE #4 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view |  |  |  |  | Rear View | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | EBC-C#1 of 1 |  |  |  |  | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9937
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [24 empty] | REAR ELEVATIONS VIEW BELOW (dimensions are in millimetres - mm)
FCP Template Code | FCP9937
Power Base Cabinet Size | 800W x 800D (x2) |  |  | Standard superstructure assembly | [39 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 800W x 800D | [7 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Power Base Cabinet #2 800W x 800D | [6 empty] | Power Base Cabinet #2 800W x 800D | [6 empty] | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #1 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  |  | L | Rear view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | [13 empty] | VU48 |  |  | VU48 |  |  |  | VU48 |  |  | VU48 | [11 empty] | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 | [11 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 | [11 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  | VU45 | [11 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 | [11 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) per Power Base Cabinet | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 | [11 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 | [11 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  | VU41 | [11 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 | [11 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | HDF Sub rack # 5 |  |  | VU39 | [13 empty] | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | [11 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU38 | [13 empty] | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 | [11 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | [11 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 | [11 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 | [11 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base #1 |  |  | VU34 | HDF Sub rack # 4 |  |  | VU34 | [13 empty] | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 | [11 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 7 |  |  | VU33 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU33 | [13 empty] | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 | [11 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 19 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 | [11 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 | [11 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 | [11 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 | HDF Sub rack # 3 |  |  | VU29 | [13 empty] | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 | [11 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU28 | [13 empty] | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 | [11 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 | [11 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 800D x 2200H |  |  |  |  | RSU2 600W x 800D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | RSU2 600W x 800D x 2200H |  |  |  | RSU1 600W x 800D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 | [11 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 2 |  |  | VU24 | [13 empty] | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 | [11 empty] | VU24 | HDF Sub rack # 7 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU23 | [13 empty] | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 | [11 empty] | VU23 | MDF Tie # 21 | MDF Tie # 20 | MDF Tie # 19 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 | [11 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 | [11 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 | [11 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [13 empty] | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 | [11 empty] | VU19 | HDF Sub rack # 6 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie #3 | VU18 | [13 empty] | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | [11 empty] | VU18 | MDF Tie # 18 | MDF Tie # 17 | MDF Tie # 16 | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  |  | VU17 | [13 empty] | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 | [11 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  |  | VU16 | [13 empty] | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 | [11 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 | [11 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 | [11 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 | [11 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #4 - (all access from front) |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #4 - (all access from front) |  | VU12 | [11 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [13 empty] | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 | [11 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 | [11 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 | [11 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 | [11 empty] | VU8 |  |  |  | VU8
The ties numbering has been changed to reflect the customers requirements |  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 | [11 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 | [11 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU5 | [11 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 | [11 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 | [11 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 | [11 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 | [11 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm |  |  | Front view |  |  | 100mm | Front view |  |  |  |  | Front view | [5 empty] | 100mm | Front view |  |  |  | 100mm |  | 100mm |  |  | Rear view |  | 100mm | Rear view |  |  |  | Rear view |  |  |  |  | 100mm |  |  | Rear view |  |  | 100mm
|  | 800mm | [7 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets) |  |  | Openreach Cabling riser | [22 empty] | Openreach Cabling riser
[5 empty] | Power Base Cabinet #1 | [18 empty] | Power Base Cabinet #2
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [12 empty] | RSU1 |  |  |  |  | RSU2
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 800W x 800D | [6 empty] | 600W x 800D |  |  |  |  | 600W x 800D | [5 empty] | 800W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [17 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8821
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [20 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8821
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [31 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [7 empty] | Customer Use Cabinet in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / Job Pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 10 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack then use Alarm and current settings sheet within Matrix |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [7 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8580
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [17 empty] | REAR ELEVATION VIEW (dimensions in millimetres - mm)
FCP Template Code | FCP8580
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [28 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [9 empty] | Customer Use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 800D | [6 empty] | Customer Use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) per Power Base Cabinet | 0 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base cabinet | 0 |  |  | VU42 | Nil inverter requested |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-rack in Power Base |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 1 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (feed to Molex in CUC2) |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (feed to Molex in CUC1) |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Created for use in Northern Ireland where ESS ac distribution capacity is available. Note - where Non-ESS use FCP9861. |  |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view |  |  |  |  | Rear view | [6 empty] | Rear view |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [9 empty] | 600mm |  |  |  |  | 600mm | [6 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 | [5 empty] | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [18 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9861
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [16 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9861
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [27 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + EBC DC
Standby AC power | Deploy when Non-ESS | Power Base Cabinet 600W x 800D | [9 empty] | EBC-C#1 of 1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU1 600W x 800D | [5 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | EBC-C#1 of 1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | 2 |  |  | VU48 |  |  |  | VU48 |  | VU48 | EBC-C battery breaker switchgear |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 | 16-Way Molex DC sub-distribution module |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil inverter provided |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-rack in Power Base |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 1 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 | HDF Sub rack # 1 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 2 |  |  | VU25 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 2 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  |  | VU19 |  | VU19 | BATTERY ENCLOSURE #6 - (all access from front) |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 | BATTERY ENCLOSURE #6 - (all access from front) |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in EBC 1 ) |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CUC 1) |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  | VU12 | BATTERY ENCLOSURE #5 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 | BATTERY ENCLOSURE #5 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | 34.9 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | 31.4 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | 38.3 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Created for use in Northern Ireland as an alternative to FCP8580 due to the necessary use of Non-ESS ac power. Requires the Expanded Battery Capacity Cabinet (EBC-C) of size 600Wx800D. |  |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  | VU5 | BATTERY ENCLOSURE #4 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 | BATTERY ENCLOSURE #4 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View |  |  |  |  | Front View | [5 empty] | Rear view |  |  |  |  | Rear View | [5 empty] | Rear view
|  | 600mm | [9 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet | [5 empty] | EBC-C#1 of 1 |  |  |  |  | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9140
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [17 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9140
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [26 empty] | Standard superstructure assembly
Standby AC power | Non-ESS | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [20 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [22 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [22 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [22 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 5 |  |  | VU44 |  |  |  | VU44 | [22 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [22 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [22 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [22 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [22 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [22 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  |  | VU38 | [22 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [22 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 | HDF sub rack # 5 |  |  | VU36 | [22 empty] | VU36 | HDF sub rack # 6 |  |  | VU36
|  |  |  | VU35 | MDF tie # 13 | MDF tie # 14 | MDF tie # 15 | VU35 | [22 empty] | VU35 | MDF tie # 18 | MDF tie # 17 | MDF tie # 16 | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [22 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 6 |  |  | VU33 |  |  |  | VU33 | [22 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 18 |  |  | VU32 |  |  |  | VU32 | [22 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 | HDF Sub rack # 3 |  |  | VU31 | [22 empty] | VU31 | HDF Sub rack # 4 |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU30 | [22 empty] | VU30 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [22 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [22 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [22 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 | HDF Sub rack # 1 |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H | [5 empty] | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 | HDF Sub rack # 2 |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU25 | [22 empty] | VU25 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 | [22 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [22 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [22 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [22 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [22 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  |  | VU19 | [22 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [22 empty] | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [22 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [22 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [22 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [22 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [22 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [22 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [22 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [22 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [22 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [22 empty] | VU8 |  |  |  | VU8
Created as an alternative to FCP9269 where Non-ESS power was offered. Note that the maximum tie cable capacity is 18 x 100 pair tie cables within the Power Base cabinet. |  |  |  | VU7 |  |  |  | VU7 | [22 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [22 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [22 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [22 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [22 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [22 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [22 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1 |  |  |  |  | RSU 2
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D |  |  |  |  | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9091
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9091
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 | HDF sub rack # 7 |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 7 |  |  | VU33 | MDF tie # 19 | MDF tie # 20 | MDF tie # 21 | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 20 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 | HDF sub rack # 5 |  |  | VU29 | [13 empty] | VU29 | HDF sub rack # 6 |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 | MDF tie # 13 | MDF tie # 14 | MDF tie # 15 | VU28 | [13 empty] | VU28 | MDF tie # 18 | MDF tie # 17 | MDF tie # 16 | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 3 |  |  | VU24 | [13 empty] | VU24 | HDF Sub rack # 4 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU23 | [13 empty] | VU23 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [13 empty] | VU19 | HDF Sub rack # 2 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [13 empty] | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [13 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [13 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [13 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Rear view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7664
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [35 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7664
Power Base Cabinet Size | 800W x 800D (x2)
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [48 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet #1 800W x 800D | [7 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Power Base Cabinet #2 800W x 800D | [6 empty] | Power Base Cabinet #2 800W x 800D | [6 empty] | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #1 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [16 empty] | Cabler riser for Customer cabling only | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48 | Cabler riser for Customer cabling only | [14 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [18 empty] | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 | [16 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [18 empty] | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 | [16 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [18 empty] | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45 | [16 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  |  | VU44 | [18 empty] | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 | [16 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [18 empty] | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 | [16 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [18 empty] | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  | VU42 | [16 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [18 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41 | [16 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [18 empty] | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 | [16 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | HDF sub rack # 5 |  |  | VU39 | [18 empty] | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 | [16 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 | MDF tie # 13 | MDF tie # 14 | MDF tie # 15 | VU38 | [18 empty] | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 | [16 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [18 empty] | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 | [16 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [18 empty] | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 | [16 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [18 empty] | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 | [16 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base #1 |  |  | VU34 | HDF sub rack # 4 |  |  | VU34 | [18 empty] | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 | [16 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 7 |  |  | VU33 | MDF tie # 10 | MDF tie # 11 | MDF tie # 12 | VU33 | [18 empty] | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 | [16 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 19 |  |  | VU32 |  |  |  | VU32 | [18 empty] | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 | [16 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 | [18 empty] | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 | [16 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [18 empty] | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 | [16 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 | HDF sub rack #3 |  |  | VU29 | [18 empty] | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 | [16 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 | MDF tie # 7 | MDF tie # 8 | MDF tie # 9 | VU28 | [18 empty] | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 | [16 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [18 empty] | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 | [16 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 800D x 2200H |  |  |  |  | RSU2 600W x 800D x 2200H |  |  |  |  | RSU3 600W x 800D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  |  | RSU3 600W x 800D x 2200H |  |  |  | RSU2 600W x 800D x 2200H |  |  |  | RSU1 600W x 800D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [18 empty] | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 | [16 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 2 |  |  | VU24 | [18 empty] | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 | [16 empty] | VU24 | HDF sub rack # 7 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU23 | [18 empty] | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 | [16 empty] | VU23 | MDF tie # 21 | MDF tie # 20 | MDF tie # 19 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [18 empty] | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 | [16 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [18 empty] | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 | [16 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [18 empty] | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 | [16 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [18 empty] | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 | [16 empty] | VU19 | HDF Sub rack # 6 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [18 empty] | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 | [16 empty] | VU18 | MDF Tie # 18 | MDF Tie # 17 | MDF Tie # 16 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [18 empty] | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 | [16 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [18 empty] | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 | [16 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [18 empty] | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 | [16 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [18 empty] | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 | [16 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [18 empty] | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 | [16 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [18 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [16 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [18 empty] | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 | [16 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [18 empty] | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 | [16 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [18 empty] | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 | [16 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [18 empty] | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 | [16 empty] | VU8 |  |  |  | VU8
The customer has requested that the MDF ties (x15) are run from the front of the Power Base Cabinet upwards then up the back upwards. The ties will be numbered from Left to Right on front and right to left on the rear |  |  |  | VU7 |  |  |  | VU7 | [18 empty] | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 | [16 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [18 empty] | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 | [16 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [18 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [16 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [18 empty] | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 | [16 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [18 empty] | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 | [16 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [18 empty] | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 | [16 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [18 empty] | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 | [16 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [22 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet #1 | [22 empty] | Power Base Cabinet #2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1 |  |  |  |  | RSU 2 |  |  |  |  | RSU3
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x800D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D | [6 empty] | 800W x800D
[6 empty] | Front | [22 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1853
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1853
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity | 2 |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 5 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1733
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1733
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [6 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 1 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 10A |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 10A |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 10A |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 10A |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 10A |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 10A |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7050
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7050
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC only - Standard System |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [7 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  | Cabler riser for Customer cabling only | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 | HDF Sub rack # 1 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
IMPORTANT - Please check job pack for location of the HDF Sub rack as one CP has requested that it is fitted in VU9-VU13 to allow space below for CP supplied Batteries and UPS (shown in red dotted lines) |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [7 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x800D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2514
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2514
Power Base Cabinet Size | 800W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [7 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) per Power Base Cabinet | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 |  |  |  | VU19 | HDF Sub rack # 2 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie #3 | VU18 |  |  |  | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm |  |  | Front view |  |  | 100mm |  | 100mm |  |  | Rear view |  |  | 100mm
|  | 800mm | [7 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets) |  |  | Openreach Cabling riser
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
800W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9609
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [11 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9609 | [9 empty] | 6-Way 3-pin AC PDU | [5 empty] | 6-Way IEC AC PDU
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only - Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [6 empty] | Customer RSU1 (600W x 600D) | [5 empty] | Customer RSU1(600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [12 empty] | VU47 |  | VU47
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 | [12 empty] | VU46 |  | VU46
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU45 |  |  |  | VU45 | [12 empty] | VU45 |  | VU45
Number of DC Systems provided | 0 |  |  | VU44 |  |  |  | VU44 | [12 empty] | VU44 | AC Power Panel & Meter | VU44
Rectifiers per DC System | 0 |  |  | VU43 |  |  |  | VU43 | [12 empty] | VU43 |  | VU43
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU42 |  |  |  | VU42 | [12 empty] | VU42 |  | VU42
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU41 |  |  |  | VU41 | [12 empty] | VU41 |  | VU41
SBSC11 Battery strings per Power Base Cabinet | 0 String(s) |  |  | VU40 |  |  |  | VU40 | [12 empty] | VU40 | AC PDU & Flex tie bar | VU40
|  |  |  | VU39 |  |  |  | VU39 | [12 empty] | VU39 |  | VU39
Customer RSU size | 600W x 600D |  |  | VU38 |  |  |  | VU38 | [12 empty] | VU38 |  | VU38
Quantity of Customer RSUs | 1 |  |  | VU37 |  |  |  | VU37 | [12 empty] | VU37 |  | VU37
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Dual Doors standard |  |  | VU36 |  |  |  | VU36 | [12 empty] | VU36 |  | VU36
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU35 |  |  |  | VU35 | [12 empty] | VU35 |  | VU35
|  |  |  | VU34 |  |  |  | VU34 | [12 empty] | VU34 |  | VU34
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU33 |  |  |  | VU33 | [12 empty] | VU33 |  | VU33
HDF Sub racks provided | 1 |  |  | VU32 |  |  |  | VU32 | [12 empty] | VU32 |  | VU32
Expected future maximum tie cables | 1 |  |  | VU31 |  |  |  | VU31 | [12 empty] | VU31 |  | VU31
Initial LLUT tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [12 empty] | VU30 |  | VU30
Initial LLUL tie cables required | 0 |  |  | VU29 | HDF Sub rack # 1 |  |  | VU29 | [12 empty] | VU29 |  | VU29
Initial LLUX tie cables required | 0 |  |  | VU28 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU28 | [12 empty] | VU28 |  | VU28
Initial LLUY tie cables required | 0 |  |  | VU27 |  |  |  | VU27 | [12 empty] | VU27 |  | VU27
|  |  |  | VU26 |  |  |  | VU26 | [12 empty] | VU26 |  | VU26
Customer Use Cabinets with doors | 0 |  |  | VU25 |  |  |  | VU25 |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU25 |  | VU25
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [12 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 | [12 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [12 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [12 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [12 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [12 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 | [12 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [12 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [12 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [12 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [12 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [12 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [12 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 | [12 empty] | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 | [12 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 | [12 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 | [12 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [12 empty] | VU8 |  | VU8
The customer has requested the provision of 1 x 6-Way 3-Pin AC PDU and 1 x 6-Way IEC AC PDU both fed from the Power Base Cabinet to be provided over first RSU space for customer to install in their own cabinet. Lower compartment will not be supplied with lock - this will be provided by the customer to their required specification. |  |  |  | VU7 |  |  |  | VU7 | [12 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [12 empty] | VU6 |  | VU6
|  |  |  | VU5 |  |  |  | VU5 | [12 empty] | VU5 |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [12 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [12 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [12 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [12 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front view | [5 empty] | Rear view |  |  |  |  | Rear view
|  | 600mm | [6 empty] | 600mm | [5 empty] | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D | [5 empty] | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9867
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [15 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9867 | [8 empty] | 6-Way 3-pin AC PDU | [14 empty] | 6-Way IEC AC PDU
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [24 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only - Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU1 (600W x 600D) |  |  |  |  | Customer RSU2(600W x 600D) | [5 empty] | Customer RSU2(600W x 600D) |  |  |  | Customer RSU1(600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [21 empty] | VU47 |  | VU47
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [21 empty] | VU46 |  | VU46
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU45 |  |  | VU45 | [21 empty] | VU45 |  | VU45
Number of DC Systems provided | 0 |  |  | VU44 |  |  | VU44 | [21 empty] | VU44 | AC Power Panel & Meter | VU44
Rectifiers per DC System | 0 |  |  | VU43 |  |  | VU43 | [21 empty] | VU43 |  | VU43
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU42 |  |  | VU42 | [21 empty] | VU42 |  | VU42
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU41 |  |  | VU41 | [21 empty] | VU41 |  | VU41
SBSC11 Battery strings per Power Base Cabinet | 0 String(s) |  |  | VU40 |  |  | VU40 | [21 empty] | VU40 | AC PDU & Flex tie bar | VU40
|  |  |  | VU39 |  |  | VU39 | [21 empty] | VU39 |  | VU39
Customer RSU size | 600W x 600D |  |  | VU38 |  |  | VU38 | [21 empty] | VU38 |  | VU38
Quantity of Customer RSUs | 2 |  |  | VU37 |  |  | VU37 | [21 empty] | VU37 |  | VU37
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Dual Doors standard |  |  | VU36 |  |  | VU36 | [21 empty] | VU36 |  | VU36
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU35 |  |  | VU35 | [21 empty] | VU35 |  | VU35
|  |  |  | VU34 |  |  | VU34 | [21 empty] | VU34 |  | VU34
Openreach HDF option requirement | HDF is not required |  |  | VU33 |  |  | VU33 | [21 empty] | VU33 |  | VU33
HDF Sub racks provided | 0 |  |  | VU32 |  |  | VU32 | [21 empty] | VU32 |  | VU32
Expected future maximum tie cables | 0 |  |  | VU31 |  |  | VU31 | [21 empty] | VU31 |  | VU31
Initial LLUT tie cables required | 0 |  |  | VU30 |  |  | VU30 | [21 empty] | VU30 |  | VU30
Initial LLUL tie cables required | 0 |  |  | VU29 |  |  | VU29 | [21 empty] | VU29 |  | VU29
Initial LLUX tie cables required | 0 |  |  | VU28 |  |  | VU28 | [21 empty] | VU28 |  | VU28
Initial LLUY tie cables required | 0 |  |  | VU27 |  |  | VU27 | [21 empty] | VU27 |  | VU27
|  |  |  | VU26 |  |  | VU26 | [21 empty] | VU26 |  | VU26
Customer Use Cabinets with doors | 0 |  |  | VU25 |  |  | VU25 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H | [5 empty] | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU25 |  | VU25
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [21 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [21 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [21 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [21 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [21 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [21 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [21 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [21 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [21 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [21 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [21 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [21 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [21 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 | [21 empty] | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 | [21 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 | [21 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 | [21 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [21 empty] | VU8 |  | VU8
The customer has requested the provision of 1 x 6-Way 3-Pin AC PDU and 1 x 6-Way IEC AC PDU both fed from the Power Base Cabinet to be provided over first RSU space for customer to install in their own cabinet. Lower compartment will not be supplied with lock - this will be provided by the customer to their required specification. |  |  |  | VU7 |  |  | VU7 | [21 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [21 empty] | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 | [21 empty] | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 | [21 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [21 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [21 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [21 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
[11 empty] | RSU 1 |  |  |  |  | RSU2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9052
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [16 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9052
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [22 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [6 empty] | Customer Use Cabinet in RSU1 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  | Customer Use Cabinet in RSU1 600W x 600D |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 6 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  | VU45 |  | VU45 |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  | VU41 |  | VU41 |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  | VU12 |  | VU12 |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  | VU5 |  | VU5 |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | Front view |  |  |  |  | Front view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Rear | [5 empty] | Rear |  |  |  |  | Rear
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  | Customer Use Cabinet on RSU 1 |  |  |  |  | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
[6 empty] | Front | [5 empty] | Front |  |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1421
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1421
Power Base Cabinet Size | 600W x 600D (x2) |  |  | Standard superstructure assembly | [9 empty] | Standard superstructure assembly | [17 empty] | Standard superstructure assembly | [5 empty] | Standard superstructure assembly | [11 empty] | Standard superstructure assembly | [9 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Power Base Cabinet #2 600W x 600D | [5 empty] | Power Base Cabinet #2 600W x 600D |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | HDF Cabinet 800W x 600D |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R | Cabler riser for Openreach Tie cables Only | L | Rear view | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [6 empty] | VU48 |  |  |  | VU48 | [13 empty] | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 | [9 empty] | VU48 |  | VU48 | [7 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [6 empty] | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 | [9 empty] | VU47 |  | VU47 | [7 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [6 empty] | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 | [9 empty] | VU46 |  | VU46 | [7 empty] | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 | [6 empty] | VU45 | HDF Sub rack # 9 |  |  | VU45 | [13 empty] | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45 | [9 empty] | VU45 |  | VU45 | [7 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [6 empty] | VU44 | MDF Tie # 25 | MDF Tie # 26 | MDF Tie # 27 | VU44 | [13 empty] | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 | [9 empty] | VU44 |  | VU44 | [7 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules)per Power Base cabinet | 1 |  |  | VU43 |  |  | VU43 | [6 empty] | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 | [9 empty] | VU43 |  | VU43 | [7 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [6 empty] | VU42 |  |  |  | VU42 | [13 empty] | VU42 | Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42 | [9 empty] | VU42 |  | VU42 | [7 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [6 empty] | VU41 |  |  |  | VU41 | [13 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41 | [9 empty] | VU41 |  | VU41 | [7 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [6 empty] | VU40 | HDF Sub rack # 8 |  |  | VU40 | [13 empty] | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 | [9 empty] | VU40 |  | VU40 | [7 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [6 empty] | VU39 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU39 | [13 empty] | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 | [9 empty] | VU39 |  | VU39 | [7 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 | [6 empty] | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 | [9 empty] | VU38 |  | VU38 | [7 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [6 empty] | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 | [9 empty] | VU37 |  | VU37 | [7 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [6 empty] | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 | [9 empty] | VU36 |  | VU36 | [7 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [6 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 | [13 empty] | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 | [9 empty] | VU35 |  | VU35 | [7 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [6 empty] | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 | [13 empty] | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 | [9 empty] | VU34 |  | VU34 | [7 empty] | VU34 |  | VU34
HDF Sub racks provided | 9 |  |  | VU33 |  |  | VU33 | [6 empty] | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 | [9 empty] | VU33 |  | VU33 | [7 empty] | VU33 |  | VU33
Expected future maximum tie cables | 27 |  |  | VU32 |  |  | VU32 | [6 empty] | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 | [9 empty] | VU32 |  | VU32 | [7 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [6 empty] | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 | [9 empty] | VU31 |  | VU31 | [7 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [6 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 | [13 empty] | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 | [9 empty] | VU30 |  | VU30 | [7 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [6 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 | [13 empty] | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 | [9 empty] | VU29 |  | VU29 | [7 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [6 empty] | VU28 |  |  |  | VU28 | [13 empty] | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 | [9 empty] | VU28 |  | VU28 | [7 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [6 empty] | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 | [9 empty] | VU27 |  | VU27 | [7 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  | VU26 |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [6 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 | [13 empty] | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 | [9 empty] | VU25 |  | VU25 | [7 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [6 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 | [13 empty] | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 | [9 empty] | VU24 |  | VU24 | [7 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [6 empty] | VU23 |  |  |  | VU23 | [13 empty] | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 | [9 empty] | VU23 |  | VU23 | [7 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [6 empty] | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 | [9 empty] | VU22 |  | VU22 | [7 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [6 empty] | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 | [9 empty] | VU21 |  | VU21 | [7 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [6 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 | [13 empty] | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 | [9 empty] | VU20 |  | VU20 | [7 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [6 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 | [13 empty] | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 | [9 empty] | VU19 |  | VU19 | [7 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [6 empty] | VU18 |  |  |  | VU18 | [13 empty] | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 | [9 empty] | VU18 |  | VU18 | [7 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [6 empty] | VU17 |  |  |  | VU17 | [13 empty] | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 | [9 empty] | VU17 |  | VU17 | [7 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [6 empty] | VU16 |  |  |  | VU16 | [13 empty] | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 | [9 empty] | VU16 |  | VU16 | [7 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [6 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 | [13 empty] | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 | [9 empty] | VU15 |  | VU15 | [7 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [6 empty] | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 | [13 empty] | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 | [9 empty] | VU14 |  | VU14 | [7 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [6 empty] | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 | [9 empty] | VU13 |  | VU13 | [7 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [6 empty] | VU12 |  |  |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [9 empty] | VU12 |  | VU12 | [7 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [6 empty] | VU11 |  |  |  | VU11 | [13 empty] | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 | [9 empty] | VU11 |  | VU11 | [7 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [6 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 | [13 empty] | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 | [9 empty] | VU10 |  | VU10 | [7 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [6 empty] | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 | [13 empty] | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 | [9 empty] | VU9 |  | VU9 | [7 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [6 empty] | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 | [9 empty] | VU8 |  | VU8 | [7 empty] | VU8 |  | VU8
Customer has requested that the MDF tie cables are installed from the bottom to the top on the front of the HDF then up the rear of the HDF. Also cables should number from left to right. |  |  |  | VU7 |  |  | VU7 | [6 empty] | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 | [9 empty] | VU7 |  | VU7 | [7 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [6 empty] | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 | [9 empty] | VU6 |  | VU6 | [7 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [6 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [9 empty] | VU5 |  | VU5 | [7 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [6 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 | [13 empty] | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 | [9 empty] | VU4 |  | VU4 | [7 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [6 empty] | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 | [9 empty] | VU3 |  | VU3 | [7 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [6 empty] | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 | [9 empty] | VU2 |  | VU2 | [7 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [6 empty] | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 | [9 empty] | VU1 |  | VU1 | [7 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | Front view | [5 empty] | Front View | [5 empty] | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | 100mm | Rear view |  |  | 100mm | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 800mm | [6 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 800mm |  |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1 | [10 empty] | HDF Cabinet | [17 empty] | Power Base Cabinet #2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | HDF | [6 empty] | RSU2 |  |  |  |  | RSU3
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D | [6 empty] | 600W x 600D |  |  |  |  | 600W x 600D | [5 empty] | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [27 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6516
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION (All dimensions are in millimetres -mm) | [15 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6516
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [23 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer Use Cabinet in RSU1 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  | Customer Use Cabinet in RSU1 600W x 600D |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  | VU45 |  | VU45 |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverters required |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  | VU41 |  | VU41 |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF is not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  | VU12 |  | VU12 |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  | VU5 |  | VU5 |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front view |  |  |  |  | Front view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Rear |  |  |  |  | Rear |  |  |  |  | Rear
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  | Customer Use Cabinet on RSU 1 |  |  |  |  | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
[11 empty] | Front |  |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3983
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [16 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3983
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [25 empty] | Standard superstructure assembly
Standby AC power | Non-ESS | Power Base Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear View | R |  | L | Rear View | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [21 empty] | Cabler riser for Customer cabling only | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [22 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [22 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [22 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 5 |  |  | VU44 |  |  | VU44 | [22 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [22 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [22 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [22 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [22 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [22 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 | [22 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [22 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [22 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [22 empty] | VU35 |  | VU35
Openreach HDF option requirement | Customer to provide in own cabinet |  |  | VU34 |  |  | VU34 | [22 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [22 empty] | VU33 |  | VU33
Expected future maximum tie cables | 20 |  |  | VU32 |  |  | VU32 | [22 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [22 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [22 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [22 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [22 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [22 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H | [5 empty] | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [22 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [22 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [22 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [22 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [22 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [22 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [22 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [22 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | The Power Base Cabinet is to be installed without right hand side panel (when viewed from the front). This will allow the MDF Tie cables to be routed as per dotted lines directly into the customer Combi-MSAN in RSU1 | [18 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [22 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [22 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [22 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [22 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [22 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [22 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [22 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [22 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [22 empty] | VU8 |  | VU8
The Power Base Cabinet is to be supplied without the right hand side panel (when viewed from the front) this will allow the MDF ties to be routed down into the right hand cable riser of the Power Base and then out into the side of the Combi-MSAN cabinet. Cables are tied to the front to back horizontal bars provided. . Note that the customer’s Combi-MSAN has cable access apertures arranged vertically on one side. |  |  |  | VU7 |  |  | VU7 | [22 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [22 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [22 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [22 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [22 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [22 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [22 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm | Front view |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  | Rear view |  |  |  |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [11 empty] | RSU 1 |  |  |  |  | RSU 2
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8407
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION (All dimensions are in millimetres -mm) | [10 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8407
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [14 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer Use Cabinet in RSU1 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU1 600W x 600D |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverters required |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF is not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front view |  |  |  |  | Rear view |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Rear |  |  |  |  | Rear
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  | Customer Use Cabinet on RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D |  |  |  | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5103
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5103
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 |  | VU45
Number of DC Systems provided | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 | AC Power Panel | VU44
Rectifiers per DC System | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  | VU42
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 |  | VU41
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 | AC PDU & Flex tie bar | VU40
|  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  | VU39
Customer RSU size | 600W x 800D |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Quantity of Customer RSUs | 0 |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Dual Doors standard |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
|  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
HDF Sub racks provided | 1 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Expected future maximum tie cables | 3 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUT tie cables required | 1 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUL tie cables required | 0 |  |  | VU29 | HDF Sub rack # 1 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUX tie cables required | 0 |  |  | VU28 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU28 |  |  |  | VU28 |  | VU28
Initial LLUY tie cables required | 0 |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
|  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
Customer Use Cabinets with doors | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
This is a Dual Door cabinet designed to give the customer a higher level of physical security for specific items of equipment within a single cabinet Access Locate / LLU PoP. A horizontal steel bulkhead is used to separate the FCP cabinet into lower and upper compartments. Cable access between the upper and lower compartments is provided using four circular openings fitted with protective grommets.This FCP product is supplied with 'Codelock1000' on the upper doors and no locks on the lower doors - The locks for the lower compartment are supplied and installed by the customer. This will give the customer full control over access to the lower compartment. |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## HDF Type 9e
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6030
Power Base Cabinet Size |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required
Standby AC power |  | HDF Type 9e Cabinet 800W x 600D | [6 empty] | HDF Type 9e Cabinet 800W x 600D
Electricity metering |  | Cabler riser for Openreach Tie cables Only | L | Front view |  |  | R | Cabler riser for Customer cabling only | Cabler riser for Customer cabling only | L | Rear view | R | Cabler riser for Openreach Tie cables Only
Initial maximum power capacity |  |  | VU48 |  |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided |  |  | VU45 | HDF Sub rack # 9 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System |  |  | VU44 | MDF Tie # 25 | MDF Tie # 26 | MDF Tie # 27 | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  | VU41
|  |  | VU40 | HDF Sub rack # 8 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size |  |  | VU39 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36
|  |  | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement |  |  | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 9 |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 27 |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required |  |  | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required |  |  | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28
|  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC |  |  | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC |  |  | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 |  |  | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 |  |  | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 |  |  | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU |  |  | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 |  |  | VU14 |  | VU14
|  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8
|  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7
|  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6
|  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 |  | VU5
|  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 |  | VU4
|  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3
|  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2
|  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) |  |  |  | HDF Type 9E | HDF Type 9e
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2788
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [14 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2788
Power Base Cabinet Size | 600W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  | Standard superstructure assembly | [20 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU1 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  | Customer Use Cabinet in RSU1 600W x 600D |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  | VU48 |  | VU48
Expected future maximum power capacity | 6 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  | VU45 |  | VU45 |  | VU45 |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  | VU42 | Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  | VU41 |  | VU41 |  | VU41 |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  | VU36
|  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  | VU28
|  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  | VU14
|  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  | VU12 |  | VU12 |  | VU12 |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  | VU9
Additional customer requirements |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  | VU8
|  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  | VU7
|  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  | VU6
|  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  | VU5 |  | VU5 |  | VU5 |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  | VU4
|  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  | VU3
|  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  | VU2
|  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  | 100mm
|  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) |  |  |  |  | Rear |  |  |  |  | Rear |  |  |  |  | Rear
Signifies FCP structure (cable management system and vertical post)
[5 empty] | Power Base Cabinet 1 |  |  | Customer Use Cabinet on RSU 1 |  |  |  |  | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option |  |  |  |  | 600W x 600D |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
[5 empty] | Front |  |  |  |  | Front |  |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## HDF Type 9Se
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7094
Power Base Cabinet Size
AC & DC Power Services Required
Standby AC power |  |  | HDF Type 9Se Cabinet 800W x 300D
Electricity metering |  |  | Cabler riser for Openreach Tie cables Only | L | Front view |  |  | R | Cabler riser for Customer cabling only
Initial maximum power capacity |  |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided |  |  |  | VU45 | HDF Sub rack # 9 |  |  | VU45
Rectifiers per DC System |  |  |  | VU44 | MDF Tie # 25 | MDF Tie # 26 | MDF Tie # 27 | VU44
Inverter chassis 750VA n+1 (2 modules) |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet |  |  |  | VU41 |  |  |  | VU41
|  |  |  | VU40 | HDF Sub rack # 8 |  |  | VU40
Customer RSU size |  |  |  | VU39 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU39
Quantity of Customer RSUs |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 | HDF Sub rack # 7 |  |  | VU35
Openreach HDF option requirement |  |  |  | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34
HDF Sub racks provided | 9 |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 27 |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required |  |  |  | VU30 | HDF Sub rack # 6 |  |  | VU30
Initial LLUX tie cables required |  |  |  | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29
Initial LLUY tie cables required |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC |  |  |  | VU25 | HDF Sub rack # 5 |  |  | VU25
6-Way IEC AC PDU in each CuC |  |  |  | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 |  |  |  | VU20 | HDF Sub rack # 4 |  |  | VU20
Ways 3 & 11 |  |  |  | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19
Ways 4 & 12 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 |  |  |  | VU15 | HDF Sub rack # 3 |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU |  |  |  | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14
|  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 | HDF Sub rack # 2 |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8
This is the HDF Type 9Se (slimline) Can be fixed against a wall or free standing with overhead fixings |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4
|  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm
800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Wall or overhead fixings
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [5 empty] | HDF Type 9Se
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
800W x 300D
Routeing of incoming Openreach tie cabling from MDF |  | Linking Basket
Front
FCP DC Power System Option Components
PLAN VIEW
Customer Use Cabinet' (CuC) Option
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## HDF Type 18e
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5471
Power Base Cabinet Size |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required
Standby AC power |  | HDF Type 18e Cabinet 800W x 600D | [6 empty] | HDF Type 18e Cabinet 800W x 600D
Electricity metering |  | Cabler riser for Openreach Tie cables Only | L | Front view |  |  | R | Cabler riser for Customer cabling only | Cabler riser for Customer cabling only | L | Rear view |  |  | R | Cabler riser for Openreach Tie cables Only
Initial maximum power capacity |  |  | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided |  |  | VU45 | HDF Sub rack # 9 |  |  | VU45 |  |  | VU45 | HDF Sub rack # 18 |  |  | VU45
Rectifiers per DC System |  |  | VU44 | MDF Tie # 25 | MDF Tie # 26 | MDF Tie # 27 | VU44 |  |  | VU44 | MDF Tie # 54 | MDF Tie # 53 | MDF Tie # 52 | VU44
Inverter chassis 750VA n+1 (2 modules) |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41
|  |  | VU40 | HDF Sub rack # 8 |  |  | VU40 |  |  | VU40 | HDF Sub rack # 17 |  |  | VU40
Customer RSU size |  |  | VU39 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU39 |  |  | VU39 | MDF Tie # 51 | MDF Tie # 50 | MDF Tie # 49 | VU39
Quantity of Customer RSUs |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36
|  |  | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 | HDF Sub rack # 16 |  |  | VU35
Openreach HDF option requirement |  |  | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 |  |  | VU34 | MDF Tie # 48 | MDF Tie # 47 | MDF Tie # 46 | VU34
HDF Sub racks provided | 18 |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 54 |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required |  |  | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 | HDF Sub rack # 15 |  |  | VU30
Initial LLUX tie cables required |  |  | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 | MDF Tie # 45 | MDF Tie # 44 | MDF Tie # 43 | VU29
Initial LLUY tie cables required |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28
|  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC |  |  | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 14 |  |  | VU25
6-Way IEC AC PDU in each CuC |  |  | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 | MDF Tie # 42 | MDF Tie # 41 | MDF Tie # 40 | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 |  |  | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 13 |  |  | VU20
Ways 3 & 11 |  |  | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 | MDF Tie # 39 | MDF Tie # 38 | MDF Tie # 37 | VU19
Ways 4 & 12 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 |  |  | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 12 |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU |  |  | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 |  |  | VU14 | MDF Tie # 36 | MDF Tie # 35 | MDF Tie # 34 | VU14
|  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 11 |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 | MDF Tie # 33 | MDF Tie # 32 | MDF Tie # 31 | VU9
Additional customer requirements |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8
|  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7
|  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6
|  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 10 |  |  | VU5
|  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 | MDF Tie # 30 | MDF Tie # 29 | MDF Tie # 28 | VU4
|  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3
|  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2
|  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [6 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) |  |  |  | HDF Type 9E | HDF Type 9e
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0112
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0112
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | 0 |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity | 0 |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Not Required |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
|  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  |  | VU4 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5397
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5397
Power Base Cabinet Size | 600W x 600D (x2) |  |  | Standard superstructure assembly | [35 empty] | Standard superstructure assembly | [5 empty] | Standard superstructure assembly | [28 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Power Base Cabinet #2 600W x 600D | [5 empty] | Power Base Cabinet #2 600W x 600D |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [32 empty] | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 | [26 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [32 empty] | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 | [26 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [32 empty] | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 | [26 empty] | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 | [32 empty] | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45 | [26 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [32 empty] | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 | [26 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules)per Power Base cabinet | 0 |  |  | VU43 |  |  | VU43 | [32 empty] | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 | [26 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 1 x ONLY IN POWER BASE #1 |  |  | VU42 | Inverter Chassis |  | VU42 | [32 empty] | VU42 | Nil Inveret |  | VU42 |  |  | VU42 |  | VU42 | [26 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [32 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41 | [26 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [32 empty] | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 | [26 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [32 empty] | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 | [26 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 6 |  |  | VU38 |  |  | VU38 | [32 empty] | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 | [26 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [32 empty] | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 | [26 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [32 empty] | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 | [26 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [32 empty] | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 | [26 empty] | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [32 empty] | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 | [26 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [32 empty] | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 | [26 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [32 empty] | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 | [26 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [32 empty] | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 | [26 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [32 empty] | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 | [26 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [32 empty] | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 | [26 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [32 empty] | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 | [26 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [32 empty] | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 | [26 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  |  | RSU5 600W x 600D x 2200H |  |  |  |  | RSU6 600W x 600D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | RSU6 600W x 600D x 2200H |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [32 empty] | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 | [26 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [32 empty] | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 | [26 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [32 empty] | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 | [26 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [32 empty] | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 | [26 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [32 empty] | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 | [26 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [32 empty] | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 | [26 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [32 empty] | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 | [26 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [32 empty] | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 | [26 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [32 empty] | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 | [26 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [32 empty] | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 | [26 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [32 empty] | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 | [26 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [32 empty] | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 | [26 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [32 empty] | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 | [26 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [32 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [26 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [32 empty] | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 | [26 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [32 empty] | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 | [26 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [32 empty] | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 | [26 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [32 empty] | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 | [26 empty] | VU8 |  | VU8
Only inverters to be fitted into Power Base #1 |  |  |  | VU7 |  |  | VU7 | [32 empty] | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 | [26 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [32 empty] | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 | [26 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [32 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [26 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [32 empty] | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 | [26 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [32 empty] | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 | [26 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [32 empty] | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 | [26 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [32 empty] | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 | [26 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Front View | [5 empty] | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1 | [36 empty] | Power Base Cabinet #2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D | [5 empty] | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [35 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8226
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [14 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8226
Power Base Cabinet Size | 600W x 600D
AC & DC Power Services Required | AC+Std DC |  |  |  | Standard superstructure assembly | [20 empty] | Standard superstructure assembly
Standby AC power | Non ESS | Power Base Cabinet 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU1 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  | Customer Use Cabinet in RSU1 600W x 600D |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  | VU48 | AC PDU & Flex tie bar | VU48 |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  | VU45 |  | VU45 |  | VU45 |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 5 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  | VU42 | Nil Inverters required |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  | VU41 |  | VU41 |  | VU41 |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  | VU36 |  | VU36
|  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  | VU28 |  | VU28
|  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  | VU19 |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 20A |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  | VU14 |  | VU14
|  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  | VU12 |  | VU12 |  | VU12 |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  | VU9 |  | VU9
Additional customer requirements |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  | VU8 |  | VU8
|  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  | VU7 |  | VU7
|  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  | VU6 |  | VU6
|  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  | VU5 |  | VU5 |  | VU5 |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  | VU4 |  | VU4
|  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  | VU3 |  | VU3
|  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  | VU2 |  | VU2
|  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  | 100mm
|  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) |  |  |  |  | Rear |  |  |  |  | Rear |  |  |  |  | Rear
Signifies FCP structure (cable management system and vertical post)
[5 empty] | Power Base Cabinet 1 |  |  | Customer Use Cabinet on RSU 1 |  |  |  |  | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option |  |  |  |  | 600W x 600D |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
[5 empty] | Front |  |  |  |  | Front |  |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7707
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [22 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7707
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [14 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [15 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | Deploy when Non-ESS | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [11 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [11 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [11 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [11 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [11 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [11 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [11 empty] | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | [11 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 5 |  |  | VU44 |  |  | VU44 | [11 empty] | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 | [11 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [11 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [11 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [11 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [11 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [11 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [11 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [11 empty] | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 | [11 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [11 empty] | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 | [11 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 | [11 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [11 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [11 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [11 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [11 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [11 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [11 empty] | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 | [11 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [11 empty] | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 | [11 empty] | VU34 |  | VU34
HDF Sub racks provided | 7 |  |  | VU33 |  |  | VU33 | [11 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [11 empty] | VU33 |  | VU33
Expected future maximum tie cables | 21 |  |  | VU32 |  |  | VU32 | [11 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [11 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [11 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [11 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [11 empty] | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 | [11 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [11 empty] | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 | [11 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [11 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [11 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [11 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [11 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [11 empty] | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 | [11 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [11 empty] | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 | [11 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [11 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [11 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [11 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [11 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [11 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [11 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [11 empty] | VU20 | HDF Sub rack # 7 |  |  | VU20 |  |  | VU20 |  |  |  | VU20 | [11 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [11 empty] | VU19 | MDF Tie # 21 | MDF Tie # 20 | MDF Tie # 19 | VU19 |  |  | VU19 |  |  |  | VU19 | [11 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [11 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [11 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [11 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [11 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [11 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [11 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [11 empty] | VU15 | HDF Sub rack # 5 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 6 |  |  | VU15 | [11 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [11 empty] | VU14 | MDF Tie # 15 | MDF Tie # 14 | MDF Tie #13 | VU14 |  |  | VU14 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie #18 | VU14 | [11 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [11 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [11 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [11 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [11 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [11 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [11 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [11 empty] | VU10 | HDF Sub rack # 3 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 4 |  |  | VU10 | [11 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [11 empty] | VU9 | MDF Tie # 9 | MDF Tie # 8 | MDF Tie # 7 | VU9 |  |  | VU9 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU9 | [11 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [11 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [11 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [11 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [11 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [11 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [11 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [11 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5 | [11 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [11 empty] | VU4 | MDF Tie # 3 | MDF Tie # 2 | MDF Tie #1 | VU4 |  |  | VU4 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU4 | [11 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [11 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [11 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [11 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [11 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [11 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [11 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9069
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9069
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC Only - Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Lockable door required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF not required |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1327
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1327
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | 2 |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 1 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0049
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [10 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0049
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [8 empty] | Customer use Cabinet in RSU2 600W x 600D | [5 empty] | Customer use Cabinet in RSU1 600W x 600D |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil inverter provided |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CUC 1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm | [5 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D |  |  |  |  | 600W x 600D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5441
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5441
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2489
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2489
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Not required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4006
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4006
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 6 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 18 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 | HDF Sub rack # 5 |  |  | VU29 | [13 empty] | VU29 | HDF Sub rack # 6 |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU28 | [13 empty] | VU28 | MDF Tie # 18 | MDF Tie # 17 | MDF Tie # 16 | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 3 |  |  | VU24 | [13 empty] | VU24 | HDF Sub rack # 4 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU23 | [13 empty] | VU23 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [13 empty] | VU19 | HDF Sub rack # 2 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [13 empty] | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [13 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [13 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [13 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2003
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [43 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2003
Power Base Cabinet Size | 600W x 800D (x2) |  |  | Standard superstructure assembly | [35 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [32 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+inverter (750VA n+1)
Standby AC power | Deploy when Non-ESS | Power Base Cabinet #1 600W x 800D | [5 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Power Base Cabinet #2 600W x 800D | [5 empty] | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | Customer RSU (600W x 800D) |  |  |  |  | HDF Cabinet 800W x 800D | [6 empty] | HDF Cabinet 800W x 800D | [6 empty] | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #2 600W x 800D |  |  |  |  | Customer RSU (600W x 800D) |  |  |  | Customer RSU (600W x 800D) |  |  |  | Power Base Cabinet #1 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [12 empty] | VU48 |  |  | VU48 | [16 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [15 empty] | VU48 |  | VU48 | [10 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [12 empty] | VU47 |  |  | VU47 | [16 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [15 empty] | VU47 |  | VU47 | [10 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [12 empty] | VU46 |  |  | VU46 | [16 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [15 empty] | VU46 |  | VU46 | [10 empty] | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 | [12 empty] | VU45 | DC Power System Chassis |  | VU45 | [16 empty] | VU45 | HDF Sub rack # 9 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | [15 empty] | VU45 | AC Power Panel & Meter | VU45 | [10 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 5 |  |  | VU44 |  |  | VU44 | [12 empty] | VU44 |  |  | VU44 | [16 empty] | VU44 | MDF Tie # 25 | MDF Tie # 26 | MDF Tie # 27 | VU44 |  |  | VU44 |  |  |  | VU44 | [15 empty] | VU44 |  | VU44 | [10 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules)per Power Base cabinet | 1 |  |  | VU43 |  |  | VU43 | [12 empty] | VU43 |  |  | VU43 | [16 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [15 empty] | VU43 |  | VU43 | [10 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules)per Power Base Cabinet | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [12 empty] | VU42 | Inverter Chassis |  | VU42 | [16 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [15 empty] | VU42 |  | VU42 | [10 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [12 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [16 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [15 empty] | VU41 | AC PDU & Flex tie bar | VU41 | [10 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [12 empty] | VU40 |  |  | VU40 | [16 empty] | VU40 | HDF Sub rack # 8 |  |  | VU40 |  |  | VU40 |  |  |  | VU40 | [15 empty] | VU40 |  | VU40 | [10 empty] | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 | [12 empty] | VU39 |  |  | VU39 | [16 empty] | VU39 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU39 |  |  | VU39 |  |  |  | VU39 | [15 empty] | VU39 |  | VU39 | [10 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 5 |  |  | VU38 |  |  | VU38 | [12 empty] | VU38 |  |  | VU38 | [16 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [15 empty] | VU38 |  | VU38 | [10 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [12 empty] | VU37 |  |  | VU37 | [16 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [15 empty] | VU37 |  | VU37 | [10 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [12 empty] | VU36 |  |  | VU36 | [16 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [15 empty] | VU36 |  | VU36 | [10 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [12 empty] | VU35 |  |  | VU35 | [16 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 |  |  |  | VU35 | [15 empty] | VU35 |  | VU35 | [10 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [12 empty] | VU34 |  |  | VU34 | [16 empty] | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 |  |  | VU34 |  |  |  | VU34 | [15 empty] | VU34 |  | VU34 | [10 empty] | VU34 |  | VU34
HDF Sub racks provided | 14 |  |  | VU33 |  |  | VU33 | [12 empty] | VU33 |  |  | VU33 | [16 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [15 empty] | VU33 |  | VU33 | [10 empty] | VU33 |  | VU33
Expected future maximum tie cables | 42 |  |  | VU32 |  |  | VU32 | [12 empty] | VU32 |  |  | VU32 | [16 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [15 empty] | VU32 |  | VU32 | [10 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [12 empty] | VU31 |  |  | VU31 | [16 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [15 empty] | VU31 |  | VU31 | [10 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [12 empty] | VU30 |  |  | VU30 | [16 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 | [15 empty] | VU30 |  | VU30 | [10 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [12 empty] | VU29 |  |  | VU29 | [16 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 |  |  |  | VU29 | [15 empty] | VU29 |  | VU29 | [10 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [12 empty] | VU28 |  |  | VU28 | [16 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [15 empty] | VU28 |  | VU28 | [10 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [12 empty] | VU27 |  |  | VU27 | [16 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [15 empty] | VU27 |  | VU27 | [10 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 800D x 2200H |  |  |  |  | RSU2 600W x 800D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | RSU3 600W x 800D x 2200H |  |  |  |  | RSU4 600W x 800D x 2200H |  |  |  |  | RSU5 600W x 800D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU5 600W x 800D x 2200H |  |  |  | RSU4 600W x 800D x 2200H |  |  |  | RSU3 600W x 800D x 2200H |  |  |  | VU26 |  | VU26 |  |  | RSU2 600W x 800D x 2200H |  |  |  | RSU1 600W x 800D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [12 empty] | VU25 |  |  | VU25 | [16 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 14 |  |  | VU25 | [15 empty] | VU25 |  | VU25 | [10 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [12 empty] | VU24 |  |  | VU24 | [16 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 | MDF Tie # 42 | MDF Tie # 41 | MDF Tie # 40 | VU24 | [15 empty] | VU24 |  | VU24 | [10 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [12 empty] | VU23 |  |  | VU23 | [16 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [15 empty] | VU23 |  | VU23 | [10 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [12 empty] | VU22 |  |  | VU22 | [16 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [15 empty] | VU22 |  | VU22 | [10 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [12 empty] | VU21 |  |  | VU21 | [16 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [15 empty] | VU21 |  | VU21 | [10 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [12 empty] | VU20 |  |  | VU20 | [16 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 13 |  |  | VU20 | [15 empty] | VU20 |  | VU20 | [10 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [12 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [16 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 | MDF Tie # 39 | MDF Tie # 38 | MDF Tie # 37 | VU19 | [15 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19 | [10 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [12 empty] | VU18 |  |  | VU18 | [16 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [15 empty] | VU18 |  | VU18 | [10 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [12 empty] | VU17 |  |  | VU17 | [16 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [15 empty] | VU17 |  | VU17 | [10 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [12 empty] | VU16 |  |  | VU16 | [16 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [15 empty] | VU16 |  | VU16 | [10 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [12 empty] | VU15 |  |  | VU15 | [16 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 12 |  |  | VU15 | [15 empty] | VU15 |  | VU15 | [10 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [12 empty] | VU14 |  |  | VU14 | [16 empty] | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 |  |  | VU14 | MDF Tie # 36 | MDF Tie # 35 | MDF Tie # 34 | VU14 | [15 empty] | VU14 |  | VU14 | [10 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [12 empty] | VU13 |  |  | VU13 | [16 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [15 empty] | VU13 |  | VU13 | [10 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [12 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [16 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [15 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [10 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [12 empty] | VU11 |  |  | VU11 | [16 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [15 empty] | VU11 |  | VU11 | [10 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [12 empty] | VU10 |  |  | VU10 | [16 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 11 |  |  | VU10 | [15 empty] | VU10 |  | VU10 | [10 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [12 empty] | VU9 |  |  | VU9 | [16 empty] | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 | MDF Tie # 33 | MDF Tie # 32 | MDF Tie # 31 | VU9 | [15 empty] | VU9 |  | VU9 | [10 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [12 empty] | VU8 |  |  | VU8 | [16 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [15 empty] | VU8 |  | VU8 | [10 empty] | VU8 |  | VU8
Customer has requested that MDF tie cables are terminated on the front of the HDF from bottom to top numbering from left to right. 2 x additional RSU spaces have been provided that can be utilised to install EBC cabinets in lieu of ESS Power when initial max power increase is requested. |  |  |  | VU7 |  |  | VU7 | [12 empty] | VU7 |  |  | VU7 | [16 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [15 empty] | VU7 |  | VU7 | [10 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [12 empty] | VU6 |  |  | VU6 | [16 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [15 empty] | VU6 |  | VU6 | [10 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [12 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [16 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 10 |  |  | VU5 | [15 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [10 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [12 empty] | VU4 |  |  | VU4 | [16 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 | MDF Tie # 30 | MDF Tie # 29 | MDF Tie # 28 | VU4 | [15 empty] | VU4 |  | VU4 | [10 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [12 empty] | VU3 |  |  | VU3 | [16 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [15 empty] | VU3 |  | VU3 | [10 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [12 empty] | VU2 |  |  | VU2 | [16 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [15 empty] | VU2 |  | VU2 | [10 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [12 empty] | VU1 |  |  | VU1 | [16 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [15 empty] | VU1 |  | VU1 | [10 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[5 empty] | Power Base Cabinet #1 | [16 empty] | Power Base Cabinet #2 | [18 empty] | HDF Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 | [10 empty] | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 800W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [15 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0805
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0805
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [32 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [29 empty] | VU48 |  | VU48
Expected future maximum power capacity | 6 |  |  | VU47 |  |  | VU47 | [29 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [29 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [29 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [29 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [29 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [29 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [29 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [29 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [29 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 | [29 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [29 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [29 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [29 empty] | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [29 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [29 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [29 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [29 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [29 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [29 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [29 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [29 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [29 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [29 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [29 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [29 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [29 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [29 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [29 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [29 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [29 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [29 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [29 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [29 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [29 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [29 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [29 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [29 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [29 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [29 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [29 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [29 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [29 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [29 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [29 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [29 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [29 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0954
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0954
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3621
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [20 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3621
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1) |  |  |  |  | Standard superstructure assembly | [31 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [7 empty] | Customer Use Cabinet in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 6 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  |  | VU46 | AC PDU & Flex tie bar | VU46 |  |  |  | VU46 | AC PDU & Flex tie bar | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 2 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
Customer has requested that both 6 way AC 3 pin PDU are fitted to the rear of the CuC's at the top. |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [7 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2266
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [5 empty] | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [15 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2266
Power Base Cabinet Size | 800W x 800D |  |  | Standard superstructure assembly | [37 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | Non ESS | Power Base Cabinet 800W x 800D | [5 empty] | Extended Battery Cabinet 800W x 800D | [8 empty] | Customer use Cabinet in RSU1 800W x 800D |  |  |  |  | Customer use Cabinet in RSU2 800W x 800D | [5 empty] | Customer use Cabinet in RSU2 800W x 800D |  |  |  |  | Customer use Cabinet in RSU1 800W x 800D |  |  |  |  | Extended Battery Cabinet 800Wx800D |  | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 6 |  |  | VU47 |  |  | VU47 |  |  | VU47 | EBC-C Battery Breaker |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 | Switchgear |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil inverter provided |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CUC 2) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CUC 1) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Non ESS option for FCP9817 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View |  |  |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view |  |  |  |  | Rear view |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 800mm | [5 empty] | 800mm | [8 empty] | 800mm |  |  |  |  | 800mm | [5 empty] | 800mm |  |  |  |  | 800mm |  |  |  |  | 800mm |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet | [5 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D |  |  |  |  | 800W x 800D |  |  |  |  | 800W x 800D
[6 empty] | FRONT | [5 empty] | FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5834
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5834
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [6 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7836
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7836
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6386
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6386
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Customer Use Cabinet 600W x 800D | [5 empty] | Customer Use Cabinet 600W x 800D |  |  |  |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors Required |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 |  |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 |  |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 |  |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 |  |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 |  |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 |  |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 |  |  |  | VU15 | HDF Sub rack # 2 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU |  |  |  | VU14 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 | HDF Sub rack # 1 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10
|  |  |  | VU9 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8
Customer has requested that space is left for customer to supply their own batteries between VU1 and VU5 - MDF ties to be terminated from VU6 to VU15 upwards both on the front of the power base cabinet. |  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5
|  |  |  | VU4 | Space reserved for customers own batteries |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 | Space reserved for customers own batteries | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Front View | [5 empty] | Front View |  |  |  |  | Rear view
|  | 600mm | [6 empty] | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
[6 empty] | Rear | [6 empty] | Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet | [6 empty] | Customer Use Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [6 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [6 empty] | Front
[6 empty] | PLAN VIEW | [6 empty] | PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## Sheet1
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP####
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 | HDF Sub rack # 2 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 | HDF Sub rack # 1 |  |  | VU10 |  |  |  | VU10 |  | VU10
|  |  |  | VU9 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
Customer has requested that space is left for customer to supply their own batteries between VU1 and VU5 - MDF ties to be terminated from VU6 to VU15 upwards both on the front of the power base cabinet. THIS IS THE SAME BUILD AS FCP0001 BUT THE CUSTOMER HAS NOW REQUESTED DOORS |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 | Space reserved for customers own batteries |  |  | VU4 |  |  |  | VU4 | Space reserved for customers own batteries | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2264
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2264
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | OR EAD & OSA Router(1 x AC each) |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 | OR 1U EAD 100/1000 (2 x DC Molex) |  |  | VU38 | [13 empty] | VU38 | GEA Brush Panel |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fibre Tray |  |  | VU37 | [13 empty] | VU37 | GEA Brush Panel |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 | Customer Equipment |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 6 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 18 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 | Customer Equipment |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 | OR EAD 10Gbps / VM TM102 10 Gbps (2 x DC Molex) |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [13 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [13 empty] | VU28 | Customer Equipment |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 | HDF Sub rack # 6 |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  | Customer Equipment |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 | MDF Tie # 18 | MDF Tie # 17 | MDF Tie # 16 | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | OR EAD Multi Slot Chassis 100/1000 (2 x DC Molex) |  |  | VU24 | [13 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [13 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 | HDF Sub rack # 5 |  |  | VU22
Ways 1 & 9 | 20A |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 | MDF Tie # 15 | MDF Tie # 14 | MDF Tie # 13 | VU21
Ways 2 & 10 | 20A |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 | [13 empty] | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [13 empty] | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 | HDF Sub rack # 3 |  |  | VU17 | [13 empty] | VU17 | HDF Sub rack # 4 |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU16 | [13 empty] | VU16 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 | [13 empty] | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 | [13 empty] | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
HDF Sub racks modified at customers request |  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## Alarm and current limit setting
Initial Load kW | Deferred alarm setting on each installed PB in a PoP (A) | Prompt alarm setting on each installed PB in a PoP (A) | Rectifier current limit setting on each installed PB in a PoP (A) | Click to RETURN TO FCP INDEX
0.5 | 7.844 | 8.7156 | 9.5872
0.6 | 9.4128 | 10.4587 | 11.5046
0.7 | 10.9817 | 12.2018 | 13.422
0.8 | 12.5505 | 13.945 | 15.3394
0.9 | 14.1193 | 15.6881 | 17.2569
1 | 15.6881 | 17.4312 | 19.1743
1.1 | 17.2569 | 19.1743 | 21.0917
1.2 | 18.8257 | 20.9174 | 23.0092
1.3 | 20.3945 | 22.6606 | 24.9266
1.4 | 21.9633 | 24.4037 | 26.844
1.5 | 23.5321 | 26.1468 | 28.7615
1.6 | 25.1009 | 27.8899 | 30.6789
1.7 | 26.6697 | 29.633 | 32.5963
1.8 | 28.2385 | 31.3761 | 34.5138
1.9 | 29.8073 | 33.1193 | 36.4312
2 | 31.3761 | 34.8624 | 38.3486
2.1 | 32.945 | 36.6055 | 40.2661
2.2 | 34.5138 | 38.3486 | 42.1835
2.3 | 36.0826 | 40.0917 | 44.1009
2.4 | 37.6514 | 41.8349 | 46.0183
2.5 | 39.2202 | 43.578 | 47.9358
2.6 | 40.789 | 45.3211 | 49.8532
2.7 | 42.3578 | 47.0642 | 51.7706
2.8 | 43.9266 | 48.8073 | 53.6881
2.9 | 45.4954 | 50.5505 | 55.6055
3 | 47.0642 | 52.2936 | 57.5229
3.1 | 48.633 | 54.0367 | 59.4404
3.2 | 50.2018 | 55.7798 | 61.3578
3.3 | 51.7706 | 57.5229 | 63.2752
3.4 | 53.3394 | 59.2661 | 65.1927
3.5 | 54.9083 | 61.0092 | 67.1101
3.6 | 56.4771 | 62.7523 | 69.0275
3.7 | 58.0459 | 64.4954 | 70.945
3.8 | 59.6147 | 66.2385 | 72.8624
3.9 | 61.1835 | 67.9817 | 74.7798
4 | 62.7523 | 69.7248 | 76.6972
4.1 | 64.3211 | 71.4679 | 78.6147
4.2 | 65.8899 | 73.211 | 80.5321
4.3 | 67.4587 | 74.9541 | 82.4495
4.4 | 69.0275 | 76.6972 | 84.367
4.5 | 70.5963 | 78.4404 | 86.2844
4.6 | 72.1651 | 80.1835 | 88.2018
4.7 | 73.7339 | 81.9266 | 90.1193
4.8 | 75.3028 | 83.6697 | 92.0367
4.9 | 76.8716 | 85.4128 | 93.9541
5 | 78.4404 | 87.156 | 95.8716
5.1 | 80.0092 | 88.8991 | 97.789
5.2 | 81.578 | 90.6422 | 99.7064
5.3 | 83.1468 | 92.3853 | 101.6239
5.4 | 84.7156 | 94.1284 | 103.5413
5.5 | 86.2844 | 95.8716 | 105.4587
5.6 | 87.8532 | 97.6147 | 107.3761
5.7 | 89.422 | 99.3578 | 109.2936
5.8 | 90.9908 | 101.1009 | 111.211
5.9 | 92.5596 | 102.844 | 113.1284
6 | 94.1284 | 104.5872 | 115.0459
6.1 | 95.6972 | 106.3303 | 116.9633
6.2 | 97.2661 | 108.0734 | 118.8807
6.3 | 98.8349 | 109.8165 | 120.7982
6.4 | 100.4037 | 111.5596 | 122.7156
6.5 | 101.9725 | 113.3028 | 124.633
6.6 | 103.5413 | 115.0459 | 126.5505
6.7 | 105.1101 | 116.789 | 128.4679
6.8 | 106.6789 | 118.5321 | 130.3853
6.9 | 108.2477 | 120.2752 | 132.3028
7 | 109.8165 | 122.0183 | 134.2202
7.1 | 111.3853 | 123.7615 | 136.1376
7.2 | 112.9541 | 125.5046 | 138.055
7.3 | 114.5229 | 127.2477 | 139.9725
7.4 | 116.0917 | 128.9908 | 141.8899
7.5 | 117.6606 | 130.7339 | 143.8073
7.6 | 119.2294 | 132.4771 | 145.7248
7.7 | 120.7982 | 134.2202 | 147.6422
7.8 | 122.367 | 135.9633 | 149.5596
7.9 | 123.9358 | 137.7064 | 151.4771
8 | 125.5046 | 139.4495 | 153.3945
8.1 | 127.0734 | 141.1927 | 155.3119
8.2 | 128.6422 | 142.9358 | 157.2294
8.3 | 130.211 | 144.6789 | 159.1468
8.4 | 131.7798 | 146.422 | 161.0642
8.5 | 133.3486 | 148.1651 | 162.9817
8.6 | 134.9174 | 149.9083 | 164.8991
8.7 | 136.4862 | 151.6514 | 166.8165
8.8 | 138.055 | 153.3945 | 168.7339
8.9 | 139.6239 | 155.1376 | 170.6514
9 | 141.1927 | 156.8807 | 172.5688
9.1 | 142.7615 | 158.6239 | 174.4862
9.2 | 144.3303 | 160.367 | 176.4037
9.3 | 145.8991 | 162.1101 | 178.3211
9.4 | 147.4679 | 163.8532 | 180.2385
9.5 | 149.0367 | 165.5963 | 182.156
9.6 | 150.6055 | 167.3394 | 184.0734
9.7 | 152.1743 | 169.0826 | 185.9908
9.8 | 153.7431 | 170.8257 | 187.9083
9.9 | 155.3119 | 172.5688 | 189.8257
10 | 156.8807 | 174.3119 | 191.7431
10.1 | 158.4495 | 176.055 | 193.6606
10.2 | 160.0183 | 177.7982 | 195.578
10.3 | 161.5872 | 179.5413 | 197.4954
10.4 | 163.156 | 181.2844 | 199.4128
10.5 | 164.7248 | 183.0275 | 201.3303
10.6 | 166.2936 | 184.7706 | 203.2477
10.7 | 167.8624 | 186.5138 | 205.1651
10.8 | 169.4312 | 188.2569 | 207.0826
10.9 | 171 | 190 | 209
11 | 172.5688 | 191.7431 | 210.9174
11.1 | 174.1376 | 193.4862 | 212.8349
11.2 | 175.7064 | 195.2294 | 214.7523
11.3 | 177.2752 | 196.9725 | 216.6697
11.4 | 178.844 | 198.7156 | 218.5872
11.5 | 180.4128 | 200.4587 | 220.5046
11.6 | 181.9817 | 202.2018 | 222.422
11.7 | 183.5505 | 203.945 | 224.3394
11.8 | 185.1193 | 205.6881 | 226.2569
11.9 | 186.6881 | 207.4312 | 228.1743
12 | 188.2569 | 209.1743 | 230.0917
12.1 | 189.8257 | 210.9174 | 232.0092
12.2 | 191.3945 | 212.6606 | 233.9266
12.3 | 192.9633 | 214.4037 | 235.844
12.4 | 194.5321 | 216.1468 | 237.7615
12.5 | 196.1009 | 217.8899 | 239.6789
12.6 | 197.6697 | 219.633 | 241.5963
12.7 | 199.2385 | 221.3761 | 243.5138
12.8 | 200.8073 | 223.1193 | 245.4312
12.9 | 202.3761 | 224.8624 | 247.3486
13 | 203.945 | 226.6055 | 249.2661
13.1 | 205.5138 | 228.3486 | 251.1835
13.2 | 207.0826 | 230.0917 | 253.1009
13.3 | 208.6514 | 231.8349 | 255.0183
13.4 | 210.2202 | 233.578 | 256.9358
13.5 | 211.789 | 235.3211 | 258.8532
13.6 | 213.3578 | 237.0642 | 260.7706
13.7 | 214.9266 | 238.8073 | 262.6881
13.8 | 216.4954 | 240.5505 | 264.6055
13.9 | 218.0642 | 242.2936 | 266.5229
14 | 219.633 | 244.0367 | 268.4404
14.1 | 221.2018 | 245.7798 | 270.3578
14.2 | 222.7706 | 247.5229 | 272.2752
14.3 | 224.3394 | 249.2661 | 274.1927
14.4 | 225.9083 | 251.0092 | 276.1101
14.5 | 227.4771 | 252.7523 | 278.0275
14.6 | 229.0459 | 254.4954 | 279.945
14.7 | 230.6147 | 256.2385 | 281.8624
14.8 | 232.1835 | 257.9817 | 283.7798
14.9 | 233.7523 | 259.7248 | 285.6972
15 | 235.3211 | 261.4679 | 287.6147
15.1 | 236.8899 | 263.211 | 289.5321
15.2 | 238.4587 | 264.9541 | 291.4495
15.3 | 240.0275 | 266.6972 | 293.367
15.4 | 241.5963 | 268.4404 | 295.2844
15.5 | 243.1651 | 270.1835 | 297.2018
15.6 | 244.7339 | 271.9266 | 299.1193
15.7 | 246.3028 | 273.6697 | 301.0367
15.8 | 247.8716 | 275.4128 | 302.9541
15.9 | 249.4404 | 277.156 | 304.8716
16 | 251.0092 | 278.8991 | 306.789
16.1 | 252.578 | 280.6422 | 308.7064
16.2 | 254.1468 | 282.3853 | 310.6239
16.3 | 255.7156 | 284.1284 | 312.5413
16.4 | 257.2844 | 285.8716 | 314.4587
16.5 | 258.8532 | 287.6147 | 316.3761
16.6 | 260.422 | 289.3578 | 318.2936
16.7 | 261.9908 | 291.1009 | 320.211
16.8 | 263.5596 | 292.844 | 322.1284
16.9 | 265.1284 | 294.5872 | 324.0459
17 | 266.6972 | 296.3303 | 325.9633
17.1 | 268.2661 | 298.0734 | 327.8807
17.2 | 269.8349 | 299.8165 | 329.7982
17.3 | 271.4037 | 301.5596 | 331.7156
17.4 | 272.9725 | 303.3028 | 333.633
17.5 | 274.5413 | 305.0459 | 335.5505
17.6 | 276.1101 | 306.789 | 337.4679
17.7 | 277.6789 | 308.5321 | 339.3853
17.8 | 279.2477 | 310.2752 | 341.3028
17.9 | 280.8165 | 312.0183 | 343.2202
18 | 282.3853 | 313.7615 | 345.1376
18.1 | 283.9541 | 315.5046 | 347.055
18.2 | 285.5229 | 317.2477 | 348.9725
18.3 | 287.0917 | 318.9908 | 350.8899
18.4 | 288.6606 | 320.7339 | 352.8073
18.5 | 290.2294 | 322.4771 | 354.7248
18.6 | 291.7982 | 324.2202 | 356.6422
18.7 | 293.367 | 325.9633 | 358.5596
18.8 | 294.9358 | 327.7064 | 360.4771
18.9 | 296.5046 | 329.4495 | 362.3945
19 | 298.0734 | 331.1927 | 364.3119
19.1 | 299.6422 | 332.9358 | 366.2294
19.2 | 301.211 | 334.6789 | 368.1468
19.3 | 302.7798 | 336.422 | 370.0642
19.4 | 304.3486 | 338.1651 | 371.9817
19.5 | 305.9174 | 339.9083 | 373.8991
19.6 | 307.4862 | 341.6514 | 375.8165
19.7 | 309.055 | 343.3945 | 377.7339
19.8 | 310.6239 | 345.1376 | 379.6514
19.9 | 312.1927 | 346.8807 | 381.5688
20 | 313.7615 | 348.6239 | 383.4862

## FCP4048
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [55 empty] | Rear Elevation
FCP Template Code | FCP4048
Power Base Cabinet Size | 2 x 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [48 empty] | Standard superstructure assembly |  |  |  |  | Standard superstructure assembly | [41 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet #1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [6 empty] | Customer Use Cabinet in RSU3 800W x 800D | [6 empty] | Customer Use Cabinet in RSU4 800W x 800D | [6 empty] | Customer Use Cabinet in RSU5 800W x 800D | [6 empty] | Customer Use Cabinet in RSU6 800W x 800D | [6 empty] | Power Base Cabinet #2 800W x 800D | [6 empty] | Power Base Cabinet #2 800W x 800D | [5 empty] | Customer Use Cabinet #6 in RSU6 800W x 800D | [5 empty] | Customer Use Cabinet#5 in RSU5 800W x 800D | [5 empty] | Customer Use Cabinet #4 in RSU4 800W x 800D | [5 empty] | Customer Use Cabinet #3 in RSU3 800W x 800D | [5 empty] | Customer Use Cabinet#2 in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet #1 in RSU1 800W x 800D | [5 empty] | Power Base Cabinet #1 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar Fed from Power Base #1 | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar Fed from Power Base #1 | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar Fed from Power Base #1 | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar Fed from Power Base #1 | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar Fed from Power Base #1 | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar Fed from Power Base #1 | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 20.0kW |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 | WARNING: Please be aware Molex ways 1-8 are fed from MCB #7 in Power Base #1 and Molex ways 9-16 are fed from MCB #7 in Power Base #2 |  | VU45 |  |  |  | VU45 | WARNING: Please be aware Molex ways 1-8 are fed from MCB #6 in Power Base #1 and Molex ways 9-16 are fed from MCB #6 in Power Base #2 |  | VU45 |  |  |  | VU45 | WARNING: Please be aware Molex ways 1-8 are fed from MCB #5 in Power Base #1 and Molex ways 9-16 are fed from MCB #5 in Power Base #2 |  | VU45 |  |  |  | VU45 | WARNING: Please be aware Molex ways 1-8 are fed from MCB #13 in Power Base #1 and Molex ways 9-16 are fed from MCB #13 in Power Base #2 |  | VU45 |  |  |  | VU45 | WARNING: Please be aware Molex ways 1-8 are fed from MCB #14 in Power Base #1 and Molex ways 9-16 are fed from MCB #14 in Power Base #2 |  | VU45 |  |  |  | VU45 | WARNING: Please be aware Molex ways 1-8 are fed from MCB #15 in Power Base #1 and Molex ways 9-16 are fed from MCB #15 in Power Base #2 |  | VU45 |  |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45 |  |  |  | VU45 | AC PDU & Flex tie bar Fed from Power Base #2 | VU45 |  |  |  | VU45 | AC PDU & Flex tie bar Fed from Power Base #2 | VU45 |  |  |  | VU45 | AC PDU & Flex tie bar Fed from Power Base #2 | VU45 |  |  |  | VU45 | AC PDU & Flex tie bar Fed from Power Base #2 | VU45 |  |  |  | VU45 | AC PDU & Flex tie bar Fed from Power Base #2 | VU45 |  |  |  | VU45 | AC PDU & Flex tie bar Fed from Power Base #2 | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) per Power Base Cabinet | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules )per Power Base Cabinet | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 6 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 6 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 2 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation Power Base Cabinet # 1 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 | 32A for Customer Kit |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 | 32A for Customer Kit |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 | 63A for Customer Kit |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 | 63A for Customer Kit |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 | 40A CuC # 3 - Molex ways 1-8 |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 | 40A CuC # 2 - Molex ways 1-8 |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 | 40A CuC # 1 - Molex ways 1-8 |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 | 40A Power Base Cabinet # 1 - Molex ways 1-8 |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
Ways 9 | 32A for Customer Kit |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Ways 10 | 32A for Customer Kit |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Ways 11 | 63A for Customer Kit |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Ways 12 | 63A for Customer Kit |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Ways 13 | 40A CuC # 4 - Molex ways 1-8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
Ways 14 | 40A CuC # 5 - Molex ways 1-8 |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
Ways 15 | 40A CuC # 6 - Molex ways 1-8 |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
Ways 16 serve Power Base mounted 16-Way Molex FDU | 40A Power Base Cabinet # 1 - Molex ways 9 -16 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
Inverter Output to AC PDU table - 'Crossover Build' |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
Power Base Cabinet #1 inverter Output (via aux socket) | CuC # 1 - AC PDU #1 |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
| CuC # 2 - AC PDU #1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
| CuC # 3 - AC PDU #1 |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
| CuC # 4 - AC PDU #1 | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
CuC # 5 - AC PDU #1
CuC # 6 - AC PDU #1
****Note: requires two AC PDUs per CuC**** | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
DC Power System Option - MCB Customisation Power Base Cabinet # 2
Ways 1 | 32A for Customer Kit
Ways 2 | 32A for Customer Kit |  |  |  |  | Power Base Cabinet #1 |  |  |  |  | Customer Use Cabinet #1 on RSU 1 | [6 empty] | Customer Use Cabinet #2 on RSU 2 | [6 empty] | Customer Use Cabinet #3 on RSU 3 | [6 empty] | Customer Use Cabinet # 4 on RSU 4 | [6 empty] | Customer Use Cabinet #5 on RSU 5 | [6 empty] | Customer Use Cabinet # 6 on RSU 6 | [8 empty] | Power Base Cabinet #2
Ways 3 | 63A for Customer Kit
Ways 4 | 63A for Customer Kit
Ways 5 | 40A CuC # 3 - Molex ways 9 -16
Ways 6 | 40A CuC # 2 - Molex ways 9 -16
Ways 7 | 40A CuC # 1 - Molex ways 9 -16
Ways 8 | 40A Power Base Cabinet # 2 - Molex ways 1-8
Ways 9 | 32A for Customer Kit
Ways 10 | 32A for Customer Kit
Ways 11 | 63A for Customer Kit
Ways 12 | 63A for Customer Kit |  |  |  |  | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D | [6 empty] | 800W x 800D | [6 empty] | 800W x 800D | [6 empty] | 800W x 800D | [6 empty] | 800W x 800D | [7 empty] | 800W x 800D
Ways 13 | 40A CuC # 4 - Molex ways 9 -16 |  |  |  |  | Front | [6 empty] | Front | [6 empty] | Front | [6 empty] | Front | [6 empty] | Front | [6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Ways 14 | 40A CuC # 5 - Molex ways 9 -16
Ways 15 | 40A CuC # 6 - Molex ways 9 -16 | PLAN VIEW
Ways 16 serve Power Base mounted 16-Way Molex FDU | 40A Power Base Cabinet # 2 - Molex ways 9 -16
Inverter Output to AC PDU table - 'Crossover Build'
Power Base Cabinet #2 inverter Output (via aux socket) | CuC # 6 - AC PDU # 2
CuC # 5 - AC PDU # 2
CuC # 4 - AC PDU # 2
CuC # 3 - AC PDU # 2
CuC # 2 - AC PDU # 2
CuC # 1 - AC PDU # 2
****Note: requires two AC PDUs per CuC****
DC Power System Option - Alarm settings - based on initial maximum power capacity
Load current major alarm setting (A) | refer to APO order / job pack
Load current minor alarm setting (A) | refer to APO order / job pack
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack
Additional customer requirements
The table above for FCP DC power fuseway allocations and 230v Inverter outputs to PDUs within each of the 6 x Customer use Cabinets (CuCs) has been agreed by the customer. FCP DC Fuse Distribution to Molex Fuse Distribution Units (FDUs) and AC PDU provision from both Power Base system cabinets into each of the six CuCs. Note: 2 x AC PDU strips per cabinet. WARNING: The supply for each AC PDU Strip must be connected to the same line (phase). Caution labels to be fitted stating "Warning of the potential 400v AC between each PDU strip".
Key to colour scheme used in layout diagrams:
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts
Note on G93: Colin Chandler: Example of caution label

## FCP6271
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6271
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 1 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1282
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1282
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC Only
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [6 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | Nil String(s) |  |  | VU41 |  |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Requested |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 0 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 0 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 0 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 0 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 0 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 0 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 0 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 0 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## Sheet2
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP####
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45
Number of DC Systems provided | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 | AC Power Panel |  |  | VU44
Rectifiers per DC System | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 | AC PDU & Flex tie bar |  |  | VU40
|  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Customer RSU size | 600W x 800D |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Quantity of Customer RSUs | 0 |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Dual Doors standard |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
|  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
HDF Sub racks provided | 2 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Expected future maximum tie cables | 5 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUT tie cables required | 1 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUL tie cables required | 0 |  |  | VU29 | HDF Sub rack # 1 |  |  | VU29 |  |  |  | VU29 | HDF Sub rack # 2 |  |  | VU29
Initial LLUX tie cables required | 0 |  |  | VU28 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU28 |  |  |  | VU28 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU28
Initial LLUY tie cables required | 0 |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
|  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
Customer Use Cabinets with doors | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
This is a Dual Door cabinet designed to give the customer a higher level of physical security for specific items of equipment within a single cabinet Access Locate / LLU PoP. A horizontal steel bulkhead is used to separate the FCP cabinet into lower and upper compartments. Cable access between the upper and lower compartments is provided using four circular openings fitted with protective grommets.This FCP product is supplied with 'Codelock1000' on the upper doors and no locks on the lower doors - The locks for the lower compartment are supplied and installed by the customer. This will give the customer full control over access to the lower compartment. |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6191
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [14 empty] | REAR ELVEATION (mm)
FCP Template Code | FCP6191
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [18 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [7 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | in Power Base Cabinet |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [7 empty] | Rear
|  |  | Openreach Cabling riser | [5 empty] | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 | [5 empty] | Customer Use Cabinet on RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [7 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6842
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6842
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | Non ESS | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 4 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 10 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [13 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [13 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 3 |  |  | VU24 | [13 empty] | VU24 | HDF Sub rack # 4 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU23 | [13 empty] | VU23 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [13 empty] | VU19 | HDF Sub rack # 2 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [13 empty] | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [13 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [13 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [13 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3389
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [16 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3389
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [27 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [9 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU2 600W x 800D | [5 empty] | Customer use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View |  |  |  |  | Front View | [5 empty] | Rear view |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [9 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet | [5 empty] | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 800D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6723
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6723
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | Non ESS | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 4 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 10 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [13 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [13 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 3 |  |  | VU24 | [13 empty] | VU24 | HDF Sub rack # 4 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU23 | [13 empty] | VU23 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 20A |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [13 empty] | VU19 | HDF Sub rack # 2 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [13 empty] | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [13 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [13 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [13 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
Non ESS option for FCP1422 |  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3594
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3594
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | Non ESS | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 6 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 18 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 | HDF Sub rack # 5 |  |  | VU29 | [13 empty] | VU29 | HDF Sub rack # 6 |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU28 | [13 empty] | VU28 | MDF Tie # 18 | MDF Tie # 17 | MDF Tie # 16 | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | HDF Sub rack # 3 |  |  | VU24 | [13 empty] | VU24 | HDF Sub rack # 4 |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU23 | [13 empty] | VU23 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 20A |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 20A |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 | [13 empty] | VU19 | HDF Sub rack # 2 |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 | [13 empty] | VU18 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 | [13 empty] | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 | [13 empty] | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 | [13 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 | [13 empty] | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6171
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6171
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 5 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 15 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [13 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [13 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 | [13 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [13 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 | HDF Sub rack # 5 |  |  | VU22 | [13 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 | [13 empty] | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [13 empty] | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 | HDF Sub rack # 3 |  |  | VU17 | [13 empty] | VU17 | HDF Sub rack # 4 |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU16 | [13 empty] | VU16 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 | [13 empty] | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 | [13 empty] | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9372
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9372
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+DC standard |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 2 |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 | [13 empty] | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 | [13 empty] | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 4 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 12 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [13 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [13 empty] | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 | [13 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [13 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 |  |  |  | VU22
Ways 1 & 9 | 20A |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 | [13 empty] | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [13 empty] | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 | HDF Sub rack # 3 |  |  | VU17 | [13 empty] | VU17 | HDF Sub rack # 4 |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU16 | [13 empty] | VU16 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 | [13 empty] | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 | [13 empty] | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3476
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [25 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3476
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [36 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer use Cabinet in RSU3 600W x 800D |  |  |  |  | Customer use Cabinet in RSU3 600W x 800D | [5 empty] | Customer use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view |  | R |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 | 6 Way AC PDU |  | VU48 |  |  | VU48 | 6 Way AC PDU |  | VU48 |  | VU48 | 6 Way AC PDU |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 3 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC |  |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 25A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 25A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 10A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 6A |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Rear view | [5 empty] | Rear view |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2 |  |  |  |  | Customer Use Cabinet in RSU3
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5547
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [21 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5547
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [30 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | RSU2 Front View 800W x 800D |  |  |  | RSU3 Front View 800W x 800D |  |  |  |  | RSU3 Rear View 800W x 800D |  | RSU2 Rear View 800W x 800D |  | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R | [16 empty] | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO Order / Job Pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 | [16 empty] | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 10 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 | [16 empty] | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 | [16 empty] | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 | [16 empty] | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 | [16 empty] | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 | [16 empty] | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 | [16 empty] | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 | [16 empty] | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 | [16 empty] | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | [16 empty] | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 | [16 empty] | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | [16 empty] | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 | [16 empty] | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 | [16 empty] | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 | [16 empty] | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 | [16 empty] | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | RSU2 800W x 800D x 2200H |  |  |  | RSU3 800W x 800D x 2200H |  |  |  | RSU3 800W x 800D x 2200H |  | RSU2 800W x 800D x 2200H |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 | [16 empty] | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 | [16 empty] | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 | [16 empty] | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 | [16 empty] | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 | [16 empty] | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 | [16 empty] | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 | [16 empty] | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 | [16 empty] | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 | [16 empty] | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 | [16 empty] | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 | [16 empty] | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 | [16 empty] | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 |  |  | VU19 | [16 empty] | VU19 |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | [16 empty] | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 | [16 empty] | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 | [16 empty] | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 | [16 empty] | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 | [16 empty] | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 | [16 empty] | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 | [16 empty] | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack then use Alarm and current settings sheet within Matrix |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 | [16 empty] | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 | [16 empty] | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 | [16 empty] | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 | [16 empty] | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 | [16 empty] | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 | [16 empty] | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 | [16 empty] | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 | [16 empty] | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 | [16 empty] | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 | [16 empty] | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 | [16 empty] | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm | [14 empty] | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm |  |  |  | 800mm |  |  |  |  | 800mm |  | 800mm |  | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [5 empty] | Rear |  |  |  | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet on RSU 1 | [5 empty] | RSU2 |  |  |  | RSU3
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D |  |  |  | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [5 empty] | Front |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2883
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [14 empty] | REAR ELVEATION (mm)
FCP Template Code | FCP2883
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1) |  |  |  |  | Standard superstructure assembly | [18 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [7 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 2 |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | in Power Base Cabinet |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [7 empty] | Rear
|  |  | Openreach Cabling riser | [5 empty] | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 | [5 empty] | Customer Use Cabinet on RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [7 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5293
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [11 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5293
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC + inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [8 empty] | Customer Use Cabinet in RSU1 600W x 800D | [6 empty] | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | 3 Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 x string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 25A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 25A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 10A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 6A |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Rear view | [6 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm | [6 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet in RSU1
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [12 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7102
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7102
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | See APO / Job pack for details |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only |  | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 2 |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 4 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 12 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 20A |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 | HDF Sub rack # 3 |  |  | VU17 |  |  |  | VU17 | HDF Sub rack # 4 |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU16 |  |  |  | VU16 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | See APO / Job pack for details |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | See APO / Job pack for details |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | See APO / Job pack for details |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8804
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [20 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8804
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [31 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [7 empty] | Customer Use Cabinet in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO Order / Job Pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 10 |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CuC2) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack then use Alarm and current settings sheet within Matrix |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [7 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6968
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6968
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [18 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC + inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 1 600W x 800D | [9 empty] | Customer Use Cabinet in RSU1 600W x 800D | [6 empty] | Customer Use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 1 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 6.0kW |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | 3 Line (phase) |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 x string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A Feeds 16-way Molex in CuC #1 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view | [6 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [9 empty] | 600mm | [6 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet 1 | [5 empty] | Customer Use Cabinet in RSU1
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [13 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2660
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2660
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO Order / Job Pack |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | 2.0kW |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO Order / Job Pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO Order / Job Pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO Order / Job Pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9258
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9258
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [5 empty] | RSU 600W x 800D | RSU 600W x 800D | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R | Front View | Rear View |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO Order / Job Pack |  |  | VU48 |  |  | VU48 |  |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | 2.0kW |  |  | VU47 |  |  | VU47 |  |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  | VU42 |  |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | RSU1 | RSU1 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | 600W x 800D x 2200H | 600W x 800D x 2200H |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO Order / Job Pack |  |  | VU11 |  |  | VU11 |  |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO Order / Job Pack |  |  | VU10 |  |  | VU10 |  |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO Order / Job Pack |  |  | VU9 |  |  | VU9 |  |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  | VU5 |  |  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View | Rear View |  | Rear view
|  | 600mm | [5 empty] | 600W x 800D | 600W x 800D | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet |  | RSU 1
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1318
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [10 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1318
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC + inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D | [5 empty] | Customer use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 6-way AC PDU (3-pin) |  | VU48 |  |  | VU48 | 6-way AC PDU (3-pin) |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 2 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 25A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 25A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 10A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 6A |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm | [5 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D |  |  |  |  | 600W x 800D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5270
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5270
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer RSU (600W x 600D) | [5 empty] | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  |  | L | Front view | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  |  | VU48 | Cabler riser for Customer cabling only | [11 empty] | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 2.0 kw |  |  | VU47 |  |  |  | VU47 | [13 empty] | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 | [13 empty] | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 | [13 empty] | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 | [13 empty] | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 | [13 empty] | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 | [13 empty] | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 | [13 empty] | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 | [13 empty] | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | OR EAD & OSA Router(1 x AC each) |  |  | VU39 | [13 empty] | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 | OR 1U EAD 100/1000 (2 x DC Molex) |  |  | VU38 | [13 empty] | VU38 | GEA Brush Panel |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fibre Tray |  |  | VU37 | [13 empty] | VU37 | GEA Brush Panel |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 | Customer Equipment |  |  | VU36 | [13 empty] | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 | [13 empty] | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 | [13 empty] | VU34 |  |  |  | VU34
HDF Sub racks provided | 4 |  |  | VU33 |  |  |  | VU33 | [13 empty] | VU33 |  |  |  | VU33
Expected future maximum tie cables | 12 |  |  | VU32 |  |  |  | VU32 | [13 empty] | VU32 | Customer Equipment |  |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 | OR EAD 10Gbps / VM TM102 10 Gbps (2 x DC Molex) |  |  | VU31 | [13 empty] | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 | [13 empty] | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 | [13 empty] | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 | [13 empty] | VU28 | Customer Equipment |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 | [13 empty] | VU27 | Space reserved for HDF Sub Rack # 6 |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  | Customer Equipment |  | VU26 |  |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 | [13 empty] | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 | OR EAD Multi Slot Chassis 100/1000 (2 x DC Molex) |  |  | VU24 | [13 empty] | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 | [13 empty] | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 | [13 empty] | VU22 | Space reserved for HDF Sub Rack # 5 |  |  | VU22
Ways 1 & 9 | 20A |  |  | VU21 |  |  |  | VU21 | [13 empty] | VU21 |  |  |  | VU21
Ways 2 & 10 | 20A |  |  | VU20 |  |  |  | VU20 | [13 empty] | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 | [13 empty] | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 | [13 empty] | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 | HDF Sub rack # 3 |  |  | VU17 | [13 empty] | VU17 | HDF Sub rack # 4 |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU16 | [13 empty] | VU16 | MDF Tie # 12 | MDF Tie # 11 | MDF Tie # 10 | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 | [13 empty] | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 | [13 empty] | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 | [13 empty] | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 | [13 empty] | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 | [13 empty] | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 | [13 empty] | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 | [13 empty] | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 | [13 empty] | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 | [13 empty] | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 | [13 empty] | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 | [13 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 | [13 empty] | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 | [13 empty] | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 | [13 empty] | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 | [13 empty] | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front view |  |  |  |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 600mm | [5 empty] | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Rear
Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise). | [12 empty] | RSU 1
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x600D | [5 empty] | 600W x 600D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0282
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [10 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0282
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet#1 in RSU1 600W x 800D | [5 empty] | Customer use Cabinet#1 in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  | VU48 | 6-way AC PDU (3-pin) |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 6.0kw |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 20A |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 10A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A Feeds 16-way Molex in CuC #1 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm | [5 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D |  |  |  |  | 600W x 800D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2182
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2182
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC only - Standard System |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [7 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  | Cabler riser for Customer cabling only | VU48 |  |  |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  |  | VU4 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm |  | 100mm | Rear view |  |  |  |  | 100mm
|  | 800mm | [7 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x800D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2438
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [13 empty] | REAR ELVEATION (mm)
FCP Template Code | FCP2438
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC |  |  |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 |  | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | 3 Line (phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 6A |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3564
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3564
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1) |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | Cabler riser for Customer cabling only | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 x String |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | NiL |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x800D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3684
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3684
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [7 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 6 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | N/A |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | N/A |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | N/A |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | N/A |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | N/A |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | N/A |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | N/A |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | N/A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5
|  |  |  | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  |  | VU4 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9005
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9005
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | single line (phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 | AC Power Panel Nil Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2201
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2201
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [6 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 6A |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 6A |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 6A |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 6A |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 6A |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 32A |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9227
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [5 empty] | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [15 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9227
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [37 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC
Standby AC power | Non ESS | Power Base Cabinet 600W x 800D | [5 empty] | Extended Battery Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU2 600W x 800D | [5 empty] | Customer use Cabinet in RSU2 600W x 800D |  |  |  |  | Customer use Cabinet in RSU1 600W x 800D |  | Extended Battery Cabinet 600W x 800D |  |  |  |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  |  | VU47 | EBC-C Battery Breaker |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 | Switchgear |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil inverter provided |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (to Molex FDU in CUC 2) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CUC 1) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8
Non ESS version of FCP0666 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View |  |  |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view |  |  |  |  | Rear view | [5 empty] | Rear View |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  | 600mm |  |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet | [5 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet in RSU1 |  |  |  |  | Customer Use Cabinet in RSU2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 800D | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  |  |  |  | 600W x 800D
[6 empty] | FRONT | [5 empty] | FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6906
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6906
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [9 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU2 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  | L | Front view |  | R |  | L | Rear view |  | R |  |  | L | Rear view |  |  | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 |  |  | VU48 |  |  | VU48 |  |  |  | VU48
Expected future maximum power capacity | 2 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter |  |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar |  |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  |  | VU34
HDF Sub racks provided | 2 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  |  | VU33
Expected future maximum tie cables | 5 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  |  | VU16
Ways 7 & 15 | 40A (feed molex in CuC1) |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 | HDF Sub rack # 2 |  |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 | MDF Tie # 6 | MDF Tie # 5 | MDF Tie # 4 | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [9 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post) | [11 empty] | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4189
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4189
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [15 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU2 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 3-Pin AC PDU |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 2 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 40A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 40A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 32A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (feed molex in CuC1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post) | [10 empty] | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3573
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3573
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [5 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 2 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 40A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 40A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 32A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6176
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6176
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  |  | VU48 |  |  |  | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | single line (phase) |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 | 6-way (3 pin) AC PDU | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 1 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | HDF Sub rack # 1 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
Provision of additional 6-way (3 pin) AC PDU to rear of Power Base Cabinet. |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) |  |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - For DC Systems ≤6kW (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6936
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6936
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | Non ESS option | Power Base Cabinet 600W x 800D | [5 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 40A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 40A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 32A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #1 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Non ESS for FCP3573 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0704
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0704
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [15 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | Non ESS Option | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU2 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 3-Pin AC PDU |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 40A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 40A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 32A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (feed molex in CuC1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #1 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Non ESS option for FCP4189 - additional rectifier required to maintain batteries |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post) | [10 empty] | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6620
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6620
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [15 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU2 600W x 800D |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | VU48 | 3-Pin AC PDU |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 2 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 40A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 40A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 32A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (feed molex in CuC1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Due to space restrictions this is a FCP4189 with a 600Wx600D Power Base Cabinet |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet | [5 empty] | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4195
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [27 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4195
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [19 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [19 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [16 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [15 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [16 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [15 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [16 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [15 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [16 empty] | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 | [15 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [16 empty] | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 | [15 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [16 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [15 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [16 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [15 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [16 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [15 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [16 empty] | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 | [15 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | EBCL fibre tray |  | VU39 | [16 empty] | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 | [15 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 3 |  |  | VU38 |  |  | VU38 | [16 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [15 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [16 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [15 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [16 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [15 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [16 empty] | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 | [15 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [16 empty] | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 | [15 empty] | VU34 |  | VU34
HDF Sub racks provided | 11 |  |  | VU33 |  |  | VU33 | [16 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [15 empty] | VU33 |  | VU33
Expected future maximum tie cables | 33 |  |  | VU32 |  |  | VU32 | [16 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [15 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  | VU31 | [16 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [15 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [16 empty] | VU30 | HDF Sub rack # 11 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 | [15 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [16 empty] | VU29 | MDF Tie # 33 | MDF Tie # 32 | MDF Tie # 31 | VU29 |  |  | VU29 |  |  |  | VU29 | [15 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [16 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [15 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [16 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [15 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [16 empty] | VU25 | HDF Sub rack # 9 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 10 |  |  | VU25 | [15 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [16 empty] | VU24 | MDF Tie # 27 | MDF Tie # 26 | MDF Tie # 25 | VU24 |  |  | VU24 | MDF Tie # 28 | MDF Tie # 29 | MDF Tie # 30 | VU24 | [15 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [16 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [15 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [16 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [15 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [16 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [15 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [16 empty] | VU20 | HDF Sub rack # 7 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 8 |  |  | VU20 | [15 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [16 empty] | VU19 | MDF Tie # 21 | MDF Tie # 20 | MDF Tie # 19 | VU19 |  |  | VU19 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU19 | [15 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [16 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [15 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [16 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [15 empty] | VU17 |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  | VU16 | [16 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [15 empty] | VU16 |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  | VU15 | [16 empty] | VU15 | HDF Sub rack # 5 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 6 |  |  | VU15 | [15 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [16 empty] | VU14 | MDF Tie # 15 | MDF Tie # 14 | MDF Tie #13 | VU14 |  |  | VU14 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie #18 | VU14 | [15 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [16 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [15 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [16 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [15 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [16 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [15 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [16 empty] | VU10 | HDF Sub rack # 3 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 4 |  |  | VU10 | [15 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [16 empty] | VU9 | MDF Tie # 9 | MDF Tie # 8 | MDF Tie # 7 | VU9 |  |  | VU9 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU9 | [15 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [16 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [15 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [16 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [15 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [16 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [15 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [16 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5 | [15 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [16 empty] | VU4 | MDF Tie # 3 | MDF Tie # 2 | MDF Tie #1 | VU4 |  |  | VU4 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU4 | [15 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [16 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [15 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [16 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [15 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [16 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [15 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7089
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [10 empty] | REAR ELEVATION
FCP Template Code | FCP7089
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [16 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC + Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D | [5 empty] | Customer use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 4 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil inverter provided |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 20A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 10A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 10A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CUC 1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View | [5 empty] | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm | [5 empty] | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 800D |  |  |  |  | 600W x 800D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4342
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [32 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4342
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [24 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [23 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [21 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [19 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [21 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [19 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [21 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [19 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [21 empty] | VU45 | HDF Sub rack # 17 |  |  | VU45 |  |  | VU45 | HDF Sub rack # 18 |  |  | VU45 | [19 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 | [21 empty] | VU44 | MDF Tie # 51 | MDF Tie # 50 | MDF Tie # 49 | VU44 |  |  | VU44 | MDF Tie # 52 | MDF Tie # 53 | MDF Tie # 54 | VU44 | [19 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [21 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [19 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [21 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [19 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [21 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [19 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [21 empty] | VU40 | HDF Sub rack # 15 |  |  | VU40 |  |  | VU40 | HDF Sub rack # 16 |  |  | VU40 | [19 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | EBCL fibre tray |  | VU39 | [21 empty] | VU39 | MDF Tie # 45 | MDF Tie # 44 | MDF Tie # 43 | VU39 |  |  | VU39 | MDF Tie # 46 | MDF Tie # 47 | MDF Tie # 48 | VU39 | [19 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 4 |  |  | VU38 |  |  | VU38 | [21 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [19 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [21 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [19 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [21 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [19 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [21 empty] | VU35 | HDF Sub rack # 13 |  |  | VU35 |  |  | VU35 | HDF Sub rack # 14 |  |  | VU35 | [19 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [21 empty] | VU34 | MDF Tie # 39 | MDF Tie # 38 | MDF Tie # 37 | VU34 |  |  | VU34 | MDF Tie # 40 | MDF Tie # 41 | MDF Tie # 42 | VU34 | [19 empty] | VU34 |  | VU34
HDF Sub racks provided | 18 |  |  | VU33 |  |  | VU33 | [21 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [19 empty] | VU33 |  | VU33
Expected future maximum tie cables | 54 |  |  | VU32 |  |  | VU32 | [21 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [19 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 8 |  |  | VU31 |  |  | VU31 | [21 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [19 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [21 empty] | VU30 | HDF Sub rack # 11 |  |  | VU30 |  |  | VU30 | HDF Sub rack # 12 |  |  | VU30 | [19 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [21 empty] | VU29 | MDF Tie # 33 | MDF Tie # 32 | MDF Tie # 31 | VU29 |  |  | VU29 | MDF Tie # 34 | MDF Tie # 35 | MDF Tie # 36 | VU29 | [19 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [21 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [19 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [21 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [19 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [21 empty] | VU25 | HDF Sub rack # 9 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 10 |  |  | VU25 | [19 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [21 empty] | VU24 | MDF Tie # 27 | MDF Tie # 26 | MDF Tie # 25 | VU24 |  |  | VU24 | MDF Tie # 28 | MDF Tie # 29 | MDF Tie # 30 | VU24 | [19 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [21 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [19 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [21 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [19 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [21 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [19 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [21 empty] | VU20 | HDF Sub rack # 7 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 8 |  |  | VU20 | [19 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3- (all access from front) |  | VU19 | [21 empty] | VU19 | MDF Tie # 21 | MDF Tie # 20 | MDF Tie # 19 | VU19 |  |  | VU19 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU19 | [19 empty] | VU19 | BATTERY ENCLOSURE #3- (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [21 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [19 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [21 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [19 empty] | VU17 |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  | VU16 | [21 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [19 empty] | VU16 |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  | VU15 | [21 empty] | VU15 | HDF Sub rack # 5 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 6 |  |  | VU15 | [19 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [21 empty] | VU14 | MDF Tie # 15 | MDF Tie # 14 | MDF Tie #13 | VU14 |  |  | VU14 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie #18 | VU14 | [19 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [21 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [19 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [21 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [19 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [21 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [19 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [21 empty] | VU10 | HDF Sub rack # 3 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 4 |  |  | VU10 | [19 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [21 empty] | VU9 | MDF Tie # 9 | MDF Tie # 8 | MDF Tie # 7 | VU9 |  |  | VU9 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU9 | [19 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [21 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [19 empty] | VU8 |  | VU8
All DC MCB's are to be 63A rated. Note - originally ordered with default MCB provision. All new orders as above. |  |  |  | VU7 |  |  | VU7 | [21 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [19 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [21 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [19 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [21 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 2 |  |  | VU5 | [19 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [21 empty] | VU4 | MDF Tie # 3 | MDF Tie # 2 | MDF Tie #1 | VU4 |  |  | VU4 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU4 | [19 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [21 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [19 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [21 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [19 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [21 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [19 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3680
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3680
Power Base Cabinet Size | 600Wx600D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 2kW |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Nil inverter |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 40A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 40A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 32A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | REAR
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D
FRONT
Optional 16-way Molex or 6-way AC PDU options within CuC |  | PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3878
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [13 empty] | REAR ELVEATION (mm)
FCP Template Code | FCP3878
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 | 3-Pin AC PDU | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | 3 Line (phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9706
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9706
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [11 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [5 empty] | Front View |  |  | Rear View |  |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R | [8 empty] | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [8 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [8 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [8 empty] | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 | [8 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 | [8 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [8 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 | [8 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 | [8 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [8 empty] | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 | [8 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 | [8 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 | [8 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [8 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | RSU 1 600Wx800Dx2200H |  |  | RSU 1 600Wx800Dx2200H |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [8 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [8 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [8 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [8 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [8 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [8 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [8 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [8 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 | [8 empty] | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [8 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [8 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [8 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [8 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [8 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [8 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [8 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [8 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [8 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [8 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [8 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [8 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [8 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 | [8 empty] | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 | [8 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 | [8 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 | [8 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [8 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [8 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [8 empty] | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 | [8 empty] | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 | [8 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [8 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [8 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [8 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [11 empty] | Rear view
|  | 600mm | [5 empty] | 600mm |  |  | 600mm |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
[6 empty] | Rear |  |  |  | Rear
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Power Base Cabinet |  |  |  | RSU1
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front |  |  |  | Front
[6 empty] | PLAN VIEW |  |  |  | PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [12 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0689
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [42 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0689
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [34 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [31 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC +Inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [31 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [27 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [31 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [27 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [31 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [27 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [31 empty] | VU45 | HDF Sub rack # 9 |  |  | VU45 |  |  | VU45 | HDF Sub rack # 18 |  |  | VU45 | [27 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 | [31 empty] | VU44 | MDF Tie # 25 | MDF Tie # 26 | MDF Tie # 27 | VU44 |  |  | VU44 | MDF Tie # 52 | MDF Tie # 53 | MDF Tie # 54 | VU44 | [27 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [31 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [27 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [31 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [27 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [31 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [27 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [31 empty] | VU40 | HDF Sub rack # 8 |  |  | VU40 |  |  | VU40 | HDF Sub rack # 17 |  |  | VU40 | [27 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [31 empty] | VU39 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU39 |  |  | VU39 | MDF Tie # 49 | MDF Tie # 51 | MDF Tie # 51 | VU39 | [27 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 6 |  |  | VU38 |  |  | VU38 | [31 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [27 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [31 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [27 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [31 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [27 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [31 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 | HDF Sub rack # 16 |  |  | VU35 | [27 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [31 empty] | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 |  |  | VU34 | MDF Tie # 46 | MDF Tie # 47 | MDF Tie # 48 | VU34 | [27 empty] | VU34 |  | VU34
HDF Sub racks provided | 18 |  |  | VU33 |  |  | VU33 | [31 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [27 empty] | VU33 |  | VU33
Expected future maximum tie cables | 54 |  |  | VU32 |  |  | VU32 | [31 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [27 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [31 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [27 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [31 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 | HDF Sub rack # 15 |  |  | VU30 | [27 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [31 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 | MDF Tie # 43 | MDF Tie # 44 | MDF Tie # 45 | VU29 | [27 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [31 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [27 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [31 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [27 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  |  | RSU5 600W x 600D x 2200H |  |  |  |  | RSU6 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU6 600W x 600D x 2200H |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [31 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 14 |  |  | VU25 | [27 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [31 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 | MDF Tie # 40 | MDF Tie # 41 | MDF Tie # 42 | VU24 | [27 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [31 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [27 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [31 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [27 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [31 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [27 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [31 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 13 |  |  | VU20 | [27 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [31 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 | MDF Tie # 37 | MDF Tie # 38 | MDF Tie # 39 | VU19 | [27 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [31 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [27 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [31 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [27 empty] | VU17 |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  | VU16 | [31 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [27 empty] | VU16 |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  | VU15 | [31 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 12 |  |  | VU15 | [27 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [31 empty] | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 |  |  | VU14 | MDF Tie # 34 | MDF Tie # 35 | MDF Tie #36 | VU14 | [27 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [31 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [27 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [31 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [27 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [31 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [27 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [31 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 11 |  |  | VU10 | [27 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [31 empty] | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 | MDF Tie # 31 | MDF Tie # 32 | MDF Tie # 33 | VU9 | [27 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [31 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [27 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [31 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [27 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [31 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [27 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [31 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 10 |  |  | VU5 | [27 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [31 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 | MDF Tie # 28 | MDF Tie # 29 | MDF Tie # 30 | VU4 | [27 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [31 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [27 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [31 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [27 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [31 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [27 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1 | [35 empty] | HDF Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | RSU6 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2096
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [42 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2096
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [34 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [31 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC +Inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [31 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [27 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [31 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [27 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [31 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [27 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [31 empty] | VU45 | HDF Sub rack # 9 |  |  | VU45 |  |  | VU45 | HDF Sub rack # 18 |  |  | VU45 | [27 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 | [31 empty] | VU44 | MDF Tie # 25 | MDF Tie # 26 | MDF Tie # 27 | VU44 |  |  | VU44 | MDF Tie # 52 | MDF Tie # 53 | MDF Tie # 54 | VU44 | [27 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [31 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [27 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [31 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [27 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [31 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [27 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [31 empty] | VU40 | HDF Sub rack # 8 |  |  | VU40 |  |  | VU40 | HDF Sub rack # 17 |  |  | VU40 | [27 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [31 empty] | VU39 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU39 |  |  | VU39 | MDF Tie # 49 | MDF Tie # 51 | MDF Tie # 51 | VU39 | [27 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 6 |  |  | VU38 |  |  | VU38 | [31 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [27 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [31 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [27 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [31 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [27 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [31 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 | HDF Sub rack # 16 |  |  | VU35 | [27 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [31 empty] | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 |  |  | VU34 | MDF Tie # 46 | MDF Tie # 47 | MDF Tie # 48 | VU34 | [27 empty] | VU34 |  | VU34
HDF Sub racks provided | 18 |  |  | VU33 |  |  | VU33 | [31 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [27 empty] | VU33 |  | VU33
Expected future maximum tie cables | 54 |  |  | VU32 |  |  | VU32 | [31 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [27 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [31 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [27 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [31 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 | HDF Sub rack # 15 |  |  | VU30 | [27 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [31 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 | MDF Tie # 43 | MDF Tie # 44 | MDF Tie # 45 | VU29 | [27 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [31 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [27 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [31 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [27 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  |  | RSU5 600W x 600D x 2200H |  |  |  |  | RSU6 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU6 600W x 600D x 2200H |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [31 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 14 |  |  | VU25 | [27 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [31 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 | MDF Tie # 40 | MDF Tie # 41 | MDF Tie # 42 | VU24 | [27 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [31 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [27 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [31 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [27 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [31 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [27 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [31 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 13 |  |  | VU20 | [27 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [31 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 | MDF Tie # 37 | MDF Tie # 38 | MDF Tie # 39 | VU19 | [27 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [31 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [27 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [31 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [27 empty] | VU17 |  | VU17
Ways 6 & 14 | 63A |  |  | VU16 |  |  | VU16 | [31 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [27 empty] | VU16 |  | VU16
Ways 7 & 15 | 63A |  |  | VU15 |  |  | VU15 | [31 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 12 |  |  | VU15 | [27 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [31 empty] | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 |  |  | VU14 | MDF Tie # 34 | MDF Tie # 35 | MDF Tie #36 | VU14 | [27 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [31 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [27 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [31 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [27 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [31 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [27 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [31 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 11 |  |  | VU10 | [27 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [31 empty] | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 | MDF Tie # 31 | MDF Tie # 32 | MDF Tie # 33 | VU9 | [27 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [31 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [27 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [31 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [27 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [31 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [27 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [31 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 10 |  |  | VU5 | [27 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [31 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 | MDF Tie # 28 | MDF Tie # 29 | MDF Tie # 30 | VU4 | [27 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [31 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [27 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [31 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [27 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [31 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [27 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1 | [35 empty] | HDF Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | RSU6 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9646
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [52 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9646
Power Base Cabinet Size | 2 x 800W x 600D |  |  | Standard superstructure assembly | [24 empty] | Standard superstructure assembly | [12 empty] | Standard superstructure assembly | [5 empty] | Standard superstructure assembly | [7 empty] | Standard superstructure assembly | [23 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  |  | Power Base Cabinet #2 800W x 600D | [5 empty] | Power Base Cabinet # 2 800W x 600D |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [21 empty] | VU48 |  |  |  | VU48 | [8 empty] | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 | [5 empty] | VU48 |  |  |  | VU48 | [19 empty] | VU48 |  | VU48
Expected future maximum power capacity | 10.1kW |  |  | VU47 |  |  | VU47 | [21 empty] | VU47 |  |  |  | VU47 | [8 empty] | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 | [5 empty] | VU47 |  |  |  | VU47 | [19 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 | [21 empty] | VU46 |  |  |  | VU46 | [8 empty] | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 | [5 empty] | VU46 |  |  |  | VU46 | [19 empty] | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 | [21 empty] | VU45 |  |  |  | VU45 | [8 empty] | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45 | [5 empty] | VU45 |  |  |  | VU45 | [19 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [21 empty] | VU44 |  |  |  | VU44 | [8 empty] | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 | [5 empty] | VU44 |  |  |  | VU44 | [19 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [21 empty] | VU43 |  |  |  | VU43 | [8 empty] | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 | [5 empty] | VU43 |  |  |  | VU43 | [19 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 | [21 empty] | VU42 |  |  |  | VU42 | [8 empty] | VU42 | Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42 | [5 empty] | VU42 |  |  |  | VU42 | [19 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [21 empty] | VU41 |  |  |  | VU41 | [8 empty] | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41 | [5 empty] | VU41 |  |  |  | VU41 | [19 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [21 empty] | VU40 |  |  |  | VU40 | [8 empty] | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 | [5 empty] | VU40 |  |  |  | VU40 | [19 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [21 empty] | VU39 |  |  |  | VU39 | [8 empty] | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 | [5 empty] | VU39 |  |  |  | VU39 | [19 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 5 |  |  | VU38 |  |  | VU38 | [21 empty] | VU38 |  |  |  | VU38 | [8 empty] | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 | [5 empty] | VU38 |  |  |  | VU38 | [19 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [21 empty] | VU37 |  |  |  | VU37 | [8 empty] | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 | [5 empty] | VU37 |  |  |  | VU37 | [19 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [21 empty] | VU36 |  |  |  | VU36 | [8 empty] | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 | [5 empty] | VU36 |  |  |  | VU36 | [19 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [21 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 | [8 empty] | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 | [5 empty] | VU35 | HDF Sub rack # 14 |  |  | VU35 | [19 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [21 empty] | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 | [8 empty] | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 | [5 empty] | VU34 | MDF Tie # 42 | MDF Tie # 41 | MDF Tie # 40 | VU34 | [19 empty] | VU34 |  | VU34
HDF Sub racks provided | 14 |  |  | VU33 |  |  | VU33 | [21 empty] | VU33 |  |  |  | VU33 | [8 empty] | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 | [5 empty] | VU33 |  |  |  | VU33 | [19 empty] | VU33 |  | VU33
Expected future maximum tie cables | 40 |  |  | VU32 |  |  | VU32 | [21 empty] | VU32 |  |  |  | VU32 | [8 empty] | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 | [5 empty] | VU32 |  |  |  | VU32 | [19 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [21 empty] | VU31 |  |  |  | VU31 | [8 empty] | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 | [5 empty] | VU31 |  |  |  | VU31 | [19 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [21 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 | [8 empty] | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 | [5 empty] | VU30 | HDF Sub rack # 13 |  |  | VU30 | [19 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [21 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 | [8 empty] | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 | [5 empty] | VU29 | MDF Tie # 39 | MDF Tie # 38 | MDF Tie # 37 | VU29 | [19 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [21 empty] | VU28 |  |  |  | VU28 | [8 empty] | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 | [5 empty] | VU28 |  |  |  | VU28 | [19 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [21 empty] | VU27 |  |  |  | VU27 | [8 empty] | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 | [5 empty] | VU27 |  |  |  | VU27 | [19 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU5 600W x 600D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | RSU5 600W x 600D x 2200H |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [21 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 | [8 empty] | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 | [5 empty] | VU25 | HDF Sub rack # 12 |  |  | VU25 | [19 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [21 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 | [8 empty] | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 | [5 empty] | VU24 | MDF Tie # 36 | MDF Tie # 35 | MDF Tie # 34 | VU24 | [19 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [21 empty] | VU23 |  |  |  | VU23 | [8 empty] | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 | [5 empty] | VU23 |  |  |  | VU23 | [19 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [21 empty] | VU22 |  |  |  | VU22 | [8 empty] | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 | [5 empty] | VU22 |  |  |  | VU22 | [19 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [21 empty] | VU21 |  |  |  | VU21 | [8 empty] | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 | [5 empty] | VU21 |  |  |  | VU21 | [19 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [21 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 | [8 empty] | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 | [5 empty] | VU20 | HDF Sub rack # 11 |  |  | VU20 | [19 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [21 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 | [8 empty] | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 | [5 empty] | VU19 | MDF Tie # 33 | MDF Tie # 32 | MDF Tie # 31 | VU19 | [19 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [21 empty] | VU18 |  |  |  | VU18 | [8 empty] | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 | [5 empty] | VU18 |  |  |  | VU18 | [19 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A(default) |  |  | VU17 |  |  | VU17 | [21 empty] | VU17 |  |  |  | VU17 | [8 empty] | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 | [5 empty] | VU17 |  |  |  | VU17 | [19 empty] | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  | VU16 | [21 empty] | VU16 |  |  |  | VU16 | [8 empty] | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 | [5 empty] | VU16 |  |  |  | VU16 | [19 empty] | VU16 |  | VU16
Ways 7 & 15 | 32A |  |  | VU15 |  |  | VU15 | [21 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 | [8 empty] | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 | [5 empty] | VU15 | HDF Sub rack # 10 |  |  | VU15 | [19 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [21 empty] | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 | [8 empty] | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 | [5 empty] | VU14 | MDF Tie # 30 | MDF Tie # 29 | MDF Tie # 28 | VU14 | [19 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [21 empty] | VU13 |  |  |  | VU13 | [8 empty] | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 | [5 empty] | VU13 |  |  |  | VU13 | [19 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [21 empty] | VU12 |  |  |  | VU12 | [8 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [5 empty] | VU12 |  |  |  | VU12 | [19 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [21 empty] | VU11 |  |  |  | VU11 | [8 empty] | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 | [5 empty] | VU11 |  |  |  | VU11 | [19 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [21 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 | [8 empty] | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 | [5 empty] | VU10 | HDF Sub rack # 9 |  |  | VU10 | [19 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [21 empty] | VU9 | MDF Tie # 45 | MDF Tie # 50 | MDF Tie # 6 | VU9 | [8 empty] | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 | [5 empty] | VU9 | MDF Tie # 27 | MDF Tie # 26 | MDF Tie # 25 | VU9 | [19 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [21 empty] | VU8 |  |  |  | VU8 | [8 empty] | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 | [5 empty] | VU8 |  |  |  | VU8 | [19 empty] | VU8 |  | VU8
Customer specific MDF tie numbering shown |  |  |  | VU7 |  |  | VU7 | [21 empty] | VU7 |  |  |  | VU7 | [8 empty] | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 | [5 empty] | VU7 |  |  |  | VU7 | [19 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [21 empty] | VU6 |  |  |  | VU6 | [8 empty] | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 | [5 empty] | VU6 |  |  |  | VU6 | [19 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [21 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 | [8 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [5 empty] | VU5 | HDF Sub rack # 8 |  |  | VU5 | [19 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [21 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie #3 | VU4 | [8 empty] | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 | [5 empty] | VU4 | MDF Tie # 24 | MDF Tie # 23 | MDF Tie # 22 | VU4 | [19 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [21 empty] | VU3 |  |  |  | VU3 | [8 empty] | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 | [5 empty] | VU3 |  |  |  | VU3 | [19 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [21 empty] | VU2 |  |  |  | VU2 | [8 empty] | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 | [5 empty] | VU2 |  |  |  | VU2 | [19 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [21 empty] | VU1 |  |  |  | VU1 | [8 empty] | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 | [5 empty] | VU1 |  |  |  | VU1 | [19 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | Front view | [5 empty] | Front View | [5 empty] | Rear view |  |  |  | Rear view |  |  |  | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 800mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 600mm |  |  |  |  | 800mm | [5 empty] | 800mm |  |  |  |  | 600mm |  |  |  | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
[5 empty] | Rear | [37 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet | [37 empty] | Power Base Cabinet # 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | HDF | [6 empty] | RSU5
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 800W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D | [6 empty] | 600W x 600D | [5 empty] | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [37 empty] | Front
[6 empty] | PLAN VIEW | [37 empty] | PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1061
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1061
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [15 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48 | 3-Pin AC PDU |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 3.0kW |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 25A |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 25A |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 10A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 6A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 6A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 6A |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post) | [10 empty] | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9030
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP9030
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [15 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  |  |  |  | Customer use Cabinet in RSU1 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | 3.0kW
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 | DC Power System Chassis |  | VU46 |  | VU46 |  |  | VU46 |  | VU46 | 3-Pin AC PDU |  | VU46 |  |  | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44 | 16-Way Molex DC sub-distribution module |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 25A |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 25A |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 10A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 6A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 6A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (Feeding Molex in CuC#1) |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Request received to move the Molex Strip in the CUC from the front to the rear of the CUC in VU45, please keep PDU in VU46. |  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post) | [10 empty] | Customer Use Cabinet in RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2750
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2750
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [17 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [8 empty] | Customer use Cabinet in RSU1 600W x 800D |  | RSU2 600W x 800D | RSU2 600W x 800D |  |  |  | Customer use Cabinet in RSU2 600W x 800D |  | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R | Front View | Rear View |  | L | Rear view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  |  |  | VU48 | 3-Pin AC PDU |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 3.0kW |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line(phase) |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  | VU41 |  |  | VU41 | RSU2 600Wx800D | RSU2 600Wx800D |  | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600Wx800D |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | not required |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 25A |  |  | VU21 |  |  | VU21 |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 25A |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 10A |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 6A |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 6A |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 6A |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front View |  |  |  |  | Front view | Rear view | Rear view | [5 empty] | Rear view
|  | 600mm | [8 empty] | 600mm |  | 600mm | 600mm |  |  |  | 600mm |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post) | [10 empty] | Customer Use Cabinet in RSU1 |  | RSU2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D |  |  |  |  | 600W x 800D |  | 600Wx800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2851
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2851
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 2.0kW |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP3707
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [18 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP3707
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [27 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer RSU (800W x 800D) | [5 empty] | Customer RSU (800W x 800D) |  |  |  | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | RSU2 800W x 800D x 2200H | [5 empty] | RSU2 800W x 800D x 2200H | [5 empty] | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 6.0kW |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 | [13 empty] | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 | [13 empty] | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 | [13 empty] | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 | [13 empty] | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 | [13 empty] | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 | [13 empty] | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 | [13 empty] | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 | [13 empty] | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | [13 empty] | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 | [13 empty] | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | [13 empty] | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 | [13 empty] | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 | [13 empty] | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 | [13 empty] | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 | [13 empty] | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 | [13 empty] | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 | [13 empty] | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 | [13 empty] | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 | [13 empty] | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 | [13 empty] | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 | [13 empty] | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 | [13 empty] | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 | [13 empty] | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 | [13 empty] | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 | [13 empty] | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 | [13 empty] | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 | [13 empty] | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 | [13 empty] | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 32A |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 | [13 empty] | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | [13 empty] | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 20A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 | [13 empty] | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 | [13 empty] | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 | [13 empty] | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 | [13 empty] | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 | [13 empty] | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 | [13 empty] | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 | [13 empty] | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 | [13 empty] | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 | [13 empty] | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 | [13 empty] | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 | [13 empty] | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 | [13 empty] | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 | [13 empty] | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 | [13 empty] | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 | [13 empty] | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 | [13 empty] | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 | [13 empty] | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm | Front view | [5 empty] | Rear view |  |  |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm |  |  |  | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [5 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1 | [7 empty] | RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [5 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8166
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [18 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8166
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1) |  |  |  |  | Standard superstructure assembly | [27 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer RSU (800W x 800D) | [5 empty] | Customer RSU (800W x 800D) |  |  |  | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  | RSU2 800W x 800D x 2200H | [5 empty] | RSU2 800W x 800D x 2200H | [5 empty] | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 | [13 empty] | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 | [13 empty] | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 | [13 empty] | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 | [13 empty] | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 | [13 empty] | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 | [13 empty] | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 | [13 empty] | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 | [13 empty] | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 | [13 empty] | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 | [13 empty] | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 | [13 empty] | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 | [13 empty] | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 | [13 empty] | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 | [13 empty] | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 | [13 empty] | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 | [13 empty] | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 | [13 empty] | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 | [13 empty] | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 | [13 empty] | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 | [13 empty] | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 | [13 empty] | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 | [13 empty] | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 | [13 empty] | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 | [13 empty] | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 | [13 empty] | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 | [13 empty] | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 | [13 empty] | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 | [13 empty] | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 32A |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 | [13 empty] | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 20A |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 | [13 empty] | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 20A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 | [13 empty] | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 6A |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 | [13 empty] | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 | [13 empty] | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 | [13 empty] | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 | [13 empty] | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 | [13 empty] | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 | [13 empty] | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 | [13 empty] | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 | [13 empty] | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 | [13 empty] | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 | [13 empty] | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 | [13 empty] | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 | [13 empty] | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 | [13 empty] | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 | [13 empty] | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 | [13 empty] | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 | [13 empty] | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm | Front view | [5 empty] | Rear view |  |  |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [5 empty] | 800mm |  |  |  | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [5 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 1 | [7 empty] | RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [5 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP8297
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [20 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP8297
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1) |  |  |  |  | Standard superstructure assembly | [31 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 1000D | [7 empty] | Customer Use Cabinet in RSU2 800W x 1000D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | 16-Way Molex DC sub-distribution module |  | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  |  | VU48 | 3-Pin AC PDU | VU48 |  |  |  | VU48 | 3-Pin AC PDU | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | 4.0kW |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 1 x 800Wx800D + 1 x 800Wx1000D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 x 800Wx800D + 1 x 800Wx1000D |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 x Only in CuC 1 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 1 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 32A |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 32A |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 32A |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 32A |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
The space allocation will comprise a footprint of 2550mm width x 1000mmdeep. This is to accommodate: a) one 800x800 FCP Power Base, b) one 800x800 FCP CuC, c) one 800W x 1000D non-standard CuC to be supplied by Eltek. This will comprise a BT spec ‘21CN’ cabinet with side panels. This will house the customer’s router device.  The power system will comprise a standard FCP DC system (4kW initial & EFM capacity) and 1500VA n+1 CE&T inverter.  One 3-pin AC PDU in each CuC  One 16-way molex and lead/fuse kit to be fitted top front of the 800x800 CuC on RSU1.  Standard FCP overhead structure and lighting system. |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [7 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [17 empty] | (21 CN Type)
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 1000D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6934
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP6934
Power Base Cabinet Size | 600W x 600D (x2) |  |  | Standard superstructure assembly | [24 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Dual System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | 600Wx600D RSU | 600Wx600D RSU | 600Wx600D RSU | 600Wx600D RSU | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D |  |  |  |  | 600Wx600D RSU | 600Wx600D RSU | 600Wx600D RSU | 600Wx600D RSU | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R | Front view | Front view | Front view | Front view |  |  | L | Front view |  | R |  |  | L | Rear view | R | Rear view | Rear view | Rear view | Rear view |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [6 empty] | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 | [6 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [6 empty] | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 | [6 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [6 empty] | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 | [6 empty] | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 | [6 empty] | VU45 |  |  | VU45 |  |  | VU45 | AC Power Panel & Meter | VU45 | [6 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 | [6 empty] | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 | [6 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [6 empty] | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 | [6 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 | [6 empty] | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 | [6 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 | [6 empty] | VU41 |  |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41 | [6 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | RSU1 | RSU2 | RSU3 | RSU4 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 | RSU4 | RSU3 | RSU2 | RSU1 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | 600Wx600Dx2200H | 600Wx600Dx2200H | 600Wx600Dx2200H | 600Wx600Dx2200H |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 | 600Wx600Dx2200H | 600Wx600Dx2200H | 600Wx600Dx2200H | 600Wx600Dx2200H |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 4 |  |  | VU38 |  |  | VU38 | [6 empty] | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 | [6 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 | [6 empty] | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 | [6 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [6 empty] | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 | [6 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [6 empty] | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 | [6 empty] | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [6 empty] | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 | [6 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [6 empty] | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 | [6 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [6 empty] | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 | [6 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [6 empty] | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 | [6 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [6 empty] | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 | [6 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [6 empty] | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 | [6 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [6 empty] | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 | [6 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [6 empty] | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 | [6 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 | [6 empty] | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 | [6 empty] | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [6 empty] | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 | [6 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [6 empty] | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 | [6 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [6 empty] | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 | [6 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [6 empty] | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 | [6 empty] | VU22 |  | VU22
Ways 1 & 9 | N/A |  |  | VU21 |  |  | VU21 | [6 empty] | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 | [6 empty] | VU21 |  | VU21
Ways 2 & 10 | N/A |  |  | VU20 |  |  | VU20 | [6 empty] | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 | [6 empty] | VU20 |  | VU20
Ways 3 & 11 | N/A |  |  | VU19 |  |  | VU19 | [6 empty] | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 | [6 empty] | VU19 |  | VU19
Ways 4 & 12 | N/A |  |  | VU18 |  |  | VU18 | [6 empty] | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 | [6 empty] | VU18 |  | VU18
Ways 5 & 13 | N/A |  |  | VU17 |  |  | VU17 | [6 empty] | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 | [6 empty] | VU17 |  | VU17
Ways 6 & 14 | N/A |  |  | VU16 |  |  | VU16 | [6 empty] | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 | [6 empty] | VU16 |  | VU16
Ways 7 & 15 | N/A |  |  | VU15 |  |  | VU15 | [6 empty] | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 | [6 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | N/A |  |  | VU14 |  |  | VU14 | [6 empty] | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 | [6 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [6 empty] | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 | [6 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 | [6 empty] | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 | [6 empty] | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 | [6 empty] | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 | [6 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 | [6 empty] | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 | [6 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 | [6 empty] | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 | [6 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [6 empty] | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 | [6 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [6 empty] | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 | [6 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [6 empty] | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 | [6 empty] | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 | [6 empty] | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 | [6 empty] | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 | [6 empty] | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 | [6 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [6 empty] | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 | [6 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [6 empty] | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 | [6 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [6 empty] | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 | [6 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [9 empty] | Front View | [5 empty] | Rear view | [8 empty] | Rear view
|  | 600mm | [5 empty] | 600mm | 600mm | 600mm | 600mm | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm | 600mm | 600mm | 600mm | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
[5 empty] | Rear | [9 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet | [9 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components | [7 empty] | 600Wx600D | 600Wx600D | 600Wx600D | 600Wx600D
[6 empty] | 600W x 600D | [9 empty] | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [9 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5554
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Consolidation) |  | FRONT AND REAR ELEVATIONS
FMC Template Code FMC0012 | FCP5554
Power Base Cabinet Size | 2 x 600W x 600D
AC & DC Power Services Required | AC +DC (1500VA inverter n+1) |  |  |  | Standard superstructure assembley | [16 empty] | Standard superstructure assembley
Standby AC power | ESS (default) | Power Base Cabinet#1 600W x 600D | [5 empty] | Power Base Cabinet#2 600W x 600D | [5 empty] | Power Base Cabinet#2 600W x 600D |  |  |  |  | Power Base Cabinet#1 600W x 600D
Electricity metering | As specified in FMC - SD |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | As per FMC-SD |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 20.0kW |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 2 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel | VU45 |  |  | VU45 | AC Power Panel | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) per Power Base Cabinet | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42 |  |  | VU42 |  | VU42
90Ah 12v FT Battery strings per Power Base Cabinet | 3 Strings |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation (generic - customised to suit FMC - SD on-site) |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 | BATTERY ENCLOSURE #3 (all access from front) |  | VU21 |  |  | VU21 | BATTERY ENCLOSURE #3 (all access from front) |  | VU21 |  |  | VU21 | BATTERY ENCLOSURE #3 (all access from front) | VU21 |  |  | VU21 | BATTERY ENCLOSURE #3 (all access from front) | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  | VU10 |  | VU10
|  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  | VU9 |  | VU9
|  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  | VU8 |  | VU8
Vendor 'from stock' Items - to be used only where required by Solution Design / Pre-installation Survey: Yellow superstructure - 'Top Hat' : Hinged Cable Ramp : Lighting Set : Floor Fixing Brackets (yellow): Electricity Meter. Istaller Consumables for use on-site - Type C MCB's (range and rating): Cable basket mesh : Fasteners & Fixings : Cables - AC, DC & CEPwork : Ferrules & crimping terminals : AC mains flexes, connectors & PDU's (IEC and 3 pin) : Kopex : DC system & inverter spares. |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View | [5 empty] | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
[6 empty] | Rear | [5 empty] | Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D | [5 empty] | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [5 empty] | Front
[6 empty] | PLAN VIEW | [5 empty] | PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1587
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Consolidation) |  | FRONT AND REAR ELEVATIONS
FMC Template Code FMC1000 | FCP1587
Power Base Cabinet Size | 1 x 600W x 600D
AC & DC Power Services Required | AC +DC (1500VA inverter n+1) |  |  |  | Standard superstructure assembley | [5 empty] | Standard superstructure assembley
Standby AC power | ESS (default) | Power Base Cabinet#1 600W x 600D | [5 empty] | Power Base Cabinet#1 600W x 600D
Electricity metering | As specified in FMC - SD |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | As per FMC-SD |  |  | VU48 |  |  | VU48 |  |  | VU48 |  | VU48
Expected future maximum power capacity | 10.0kW |  |  | VU47 |  |  | VU47 |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  | VU45 | AC Power Panel | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) per Power Base Cabinet | 0 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  | VU42 |  | VU42
90Ah 12v FT Battery strings per Power Base Cabinet | 3 Strings |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation (generic - customised to suit FMC - SD on-site) |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 | BATTERY ENCLOSURE #3 (all access from front) |  | VU21 |  |  | VU21 | BATTERY ENCLOSURE #3 (all access from front) | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
|  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
|  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
Vendor 'from stock' Items - to be used only where required by Solution Design / Pre-installation Survey: Yellow superstructure - 'Top Hat' : Hinged Cable Ramp : Lighting Set : Floor Fixing Brackets (yellow): Electricity Meter. Istaller Consumables for use on-site - Type C MCB's (range and rating): Cable basket mesh : Fasteners & Fixings : Cables - AC, DC & CEPwork : Ferrules & crimping terminals : AC mains flexes, connectors & PDU's (IEC and 3 pin) : Kopex : DC system & inverter spares. |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9597
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Consolidation) |  | FRONT AND REAR ELEVATIONS
FMC Template Code FMC1000 | FCP9597
Power Base Cabinet Size | 1 x 600W x 800D
AC & DC Power Services Required | AC +DC (750VA inverter n+1) |  |  |  | Standard superstructure assembley | [5 empty] | Standard superstructure assembley
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [5 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 | DC Power System Chassis |  | VU46 |  |  | VU46 | AC Power Panel | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) per Power Base Cabinet | 1 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 0 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
90Ah 12v FT Battery strings per Power Base Cabinet | 2 Strings |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2- (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
|  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
|  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2536
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Consolidation) |  | FRONT R ELEVATIONS | [16 empty] | REAR ELEVATION
FMC Template Code | FCP2536
Power Base Cabinet Size | 600W x 800D
AC & DC Power Services Required | AC +DC (750VA inverter n+1) |  |  |  | Standard superstructure assembley | [17 empty] | Standard superstructure assembley
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [5 empty] | RSU1 CuC 600Wx800D | [5 empty] | RSU1 CuC 600Wx800D | [5 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 | DC Power System Chassis |  | VU46 |  |  | VU46 |  |  | VU46 |  |  | VU46 | 6 way IEC AC PDU | VU46 |  |  |  | VU46 | AC Power Panel | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  |  | VU44 | Fixing Bar | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) per Power Base Cabinet | 1 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) per Power Base Cabinet | 0 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
90Ah 12v FT Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 1 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 20A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 20A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
|  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
|  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Front View | [5 empty] | Rear View | [5 empty] | Rear view
|  | 600mm | [5 empty] | 600mm | [5 empty] | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
[6 empty] | Rear | [5 empty] | Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet | [5 empty] | RSU1 CuC
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 800D | [5 empty] | 600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [5 empty] | Front
[6 empty] | PLAN VIEW | [5 empty] | PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2906
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP2906
Power Base Cabinet Size | 800W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | 2
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  |  | VU43 | AC Power Panel & Meter | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | None |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 10A |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 10A |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 6A |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 6A |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear View
|  | 800mm | [6 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9632
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP9632
Power Base Cabinet Size | 800W x 6800D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [5 empty] | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | 2
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  | VU43 | AC Power Panel & Meter | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Nil Inverter |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | None |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 40A (default) |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 40A (default) |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 32A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 32A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear View
|  | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 600D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7885
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7885
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC only - Standard System |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack | [8 empty] | Cabler riser for Customer cabling only
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x800D
Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9672
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP9672
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+ DC
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  | VU43 | AC Power Panel & Meter | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Nil Inverter |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear View
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9158
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP9158
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | 2
AC Supply type (actual design is subject to BT survey) | Single Line (phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  |  | VU43 | AC Power Panel & Meter | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | None |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear View
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4482
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP4482
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Unmetered |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  | VU43 | AC Power Panel | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear View
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7417
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP7417
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [5 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  | VU43 | AC Power Panel & Meter | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear View
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 600D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5642
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP5642
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [5 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Unmetered |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  | VU43 | AC Power Panel | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear View
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 600D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0019
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [42 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0019
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [34 empty] | Standard superstructure assembly | [6 empty] | Standard superstructure assembly | [31 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC +Inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | HDF Cabinet 800W x 600D | [6 empty] | HDF Cabinet 800W x 600D | [6 empty] | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R | Cabler riser for Customer cabling only | L | Front view |  |  | R | Cabler riser for Openreach Tie cables Only | Cabler riser for Openreach Tie cables Only | L | Rear view |  |  | R | Cabler riser for Customer cabling only |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  |  | VU48 |  |  | VU48 | [31 empty] | VU48 |  |  |  | VU48 |  |  | VU48 |  |  |  | VU48 | [27 empty] | VU48 |  | VU48
Expected future maximum power capacity | refer to APO order / job pack |  |  | VU47 |  |  | VU47 | [31 empty] | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 | [27 empty] | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [31 empty] | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | [27 empty] | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 | [31 empty] | VU45 | HDF Sub rack # 9 |  |  | VU45 |  |  | VU45 | HDF Sub rack # 18 |  |  | VU45 | [27 empty] | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 | [31 empty] | VU44 | MDF Tie # 25 | MDF Tie # 26 | MDF Tie # 27 | VU44 |  |  | VU44 | MDF Tie # 52 | MDF Tie # 53 | MDF Tie # 54 | VU44 | [27 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [31 empty] | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | [27 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 | [31 empty] | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 | [27 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 | [31 empty] | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 | [27 empty] | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 | [31 empty] | VU40 | HDF Sub rack # 8 |  |  | VU40 |  |  | VU40 | HDF Sub rack # 17 |  |  | VU40 | [27 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 |  |  | VU39 | [31 empty] | VU39 | MDF Tie # 22 | MDF Tie # 23 | MDF Tie # 24 | VU39 |  |  | VU39 | MDF Tie # 49 | MDF Tie # 51 | MDF Tie # 51 | VU39 | [27 empty] | VU39 |  | VU39
Quantity of Customer RSUs | 6 |  |  | VU38 |  |  | VU38 | [31 empty] | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 | [27 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 | [31 empty] | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | [27 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [31 empty] | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 | [27 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [31 empty] | VU35 | HDF Sub rack # 7 |  |  | VU35 |  |  | VU35 | HDF Sub rack # 16 |  |  | VU35 | [27 empty] | VU35 |  | VU35
Openreach HDF option requirement | 1 |  |  | VU34 |  |  | VU34 | [31 empty] | VU34 | MDF Tie # 19 | MDF Tie # 20 | MDF Tie # 21 | VU34 |  |  | VU34 | MDF Tie # 46 | MDF Tie # 47 | MDF Tie # 48 | VU34 | [27 empty] | VU34 |  | VU34
HDF Sub racks provided | 18 |  |  | VU33 |  |  | VU33 | [31 empty] | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 | [27 empty] | VU33 |  | VU33
Expected future maximum tie cables | 54 |  |  | VU32 |  |  | VU32 | [31 empty] | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 | [27 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [31 empty] | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 | [27 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [31 empty] | VU30 | HDF Sub rack # 6 |  |  | VU30 |  |  | VU30 | HDF Sub rack # 15 |  |  | VU30 | [27 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [31 empty] | VU29 | MDF Tie # 16 | MDF Tie # 17 | MDF Tie # 18 | VU29 |  |  | VU29 | MDF Tie # 43 | MDF Tie # 44 | MDF Tie # 45 | VU29 | [27 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [31 empty] | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 | [27 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [31 empty] | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 | [27 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  |  | RSU5 600W x 600D x 2200H |  |  |  |  | RSU6 600W x 600D x 2200H |  |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  |  | RSU6 600W x 600D x 2200H |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [31 empty] | VU25 | HDF Sub rack # 5 |  |  | VU25 |  |  | VU25 | HDF Sub rack # 14 |  |  | VU25 | [27 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [31 empty] | VU24 | MDF Tie # 13 | MDF Tie # 14 | MDF Tie # 15 | VU24 |  |  | VU24 | MDF Tie # 40 | MDF Tie # 41 | MDF Tie # 42 | VU24 | [27 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [31 empty] | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 | [27 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [31 empty] | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 | [27 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [31 empty] | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 | [27 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [31 empty] | VU20 | HDF Sub rack # 4 |  |  | VU20 |  |  | VU20 | HDF Sub rack # 13 |  |  | VU20 | [27 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [31 empty] | VU19 | MDF Tie # 10 | MDF Tie # 11 | MDF Tie # 12 | VU19 |  |  | VU19 | MDF Tie # 37 | MDF Tie # 38 | MDF Tie # 39 | VU19 | [27 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [31 empty] | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 | [27 empty] | VU18 |  | VU18
Ways 5 & 13 | 63A |  |  | VU17 |  |  | VU17 | [31 empty] | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 | [27 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 | [31 empty] | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 | [27 empty] | VU16 |  | VU16
Ways 7 & 15 | 40 |  |  | VU15 |  |  | VU15 | [31 empty] | VU15 | HDF Sub rack # 3 |  |  | VU15 |  |  | VU15 | HDF Sub rack # 12 |  |  | VU15 | [27 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [31 empty] | VU14 | MDF Tie # 7 | MDF Tie # 8 | MDF Tie # 9 | VU14 |  |  | VU14 | MDF Tie # 34 | MDF Tie # 35 | MDF Tie #36 | VU14 | [27 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [31 empty] | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 | [27 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [31 empty] | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 | [27 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [31 empty] | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 | [27 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [31 empty] | VU10 | HDF Sub rack # 2 |  |  | VU10 |  |  | VU10 | HDF Sub rack # 11 |  |  | VU10 | [27 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [31 empty] | VU9 | MDF Tie # 4 | MDF Tie # 5 | MDF Tie # 6 | VU9 |  |  | VU9 | MDF Tie # 31 | MDF Tie # 32 | MDF Tie # 33 | VU9 | [27 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [31 empty] | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 | [27 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [31 empty] | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 | [27 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [31 empty] | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 | [27 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [31 empty] | VU5 | HDF Sub rack # 1 |  |  | VU5 |  |  | VU5 | HDF Sub rack # 10 |  |  | VU5 | [27 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [31 empty] | VU4 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU4 |  |  | VU4 | MDF Tie # 28 | MDF Tie # 29 | MDF Tie # 30 | VU4 | [27 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [31 empty] | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 | [27 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [31 empty] | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 | [27 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [31 empty] | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 | [27 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | 100mm | Front view |  |  |  |  | 100mm | 100mm | Rear view |  |  |  |  | 100mm | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 800mm | [6 empty] | 800mm | [6 empty] | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1 | [35 empty] | HDF Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | RSU6 |  |  |  |  | HDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 800W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5262
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT & REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP5262
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC only - Standard System |  |  | Standard superstructure assembly | [11 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | RSU1 800Wx800D Front |  |  | RSU1 800Wx800D Rear |  | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R | [8 empty] | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack | [13 empty] | Cabler riser for Customer cabling only
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 | [8 empty] | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 | [8 empty] | VU45 |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 | [8 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [8 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 | [8 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 | [8 empty] | VU41 |  | VU41
|  |  |  | VU40 |  |  | VU40 | [8 empty] | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 | [8 empty] | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 | [8 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 | [8 empty] | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [8 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [8 empty] | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [8 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [8 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | RSU 1 800W x 800D x 2200H |  |  | RSU 1 800W x 800D x 2200H |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [8 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [8 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [8 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [8 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [8 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 | [8 empty] | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [8 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [8 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [8 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [8 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [8 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [8 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [8 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [8 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [8 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [8 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [8 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [8 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [8 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 | [8 empty] | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 | [8 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 | [8 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | N/A |  |  | VU9 |  |  | VU9 | [8 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [8 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [8 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [8 empty] | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 | [8 empty] | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 | [8 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [8 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [8 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [8 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm | [6 empty] | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm |  |  | 800mm |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear |  |  |  |  | Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet 1 |  |  |  |  | RSU1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x800D |  |  |  |  | 800W x 800D
[6 empty] | Front |  |  |  |  | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4415
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [12 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4415
Power Base Cabinet Size | 800W x 600D
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1) |  |  |  |  | Standard superstructure assembly | [14 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 600D | [7 empty] | Customer Use Cabinet in RSU2 600W x 600D |  |  |  |  | Customer Use Cabinet in RSU2 600W x 600D |  |  |  | Power Base Cabinet 800W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  | L | Front view |  | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack |  | Cable riser for Openreach Ties and fibre cables only | [5 empty] | Cable riser for Customer cabling only | [10 empty] | Cable riser for Customer cabling only |  |  |  | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 | DC Power System Chassis |  |  | VU46 |  |  | VU46 | 16-Way Molex DC sub-distribution module |  | VU46 |  | VU46 |  | VU46 |  |  | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  |  | VU40 |  |  | VU40 |  |  | VU40 |  | VU40 |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  |  | VU39 |  |  | VU39 |  |  | VU39 |  | VU39 |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  |  | VU37 |  |  | VU37 |  |  | VU37 |  | VU37 |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 1 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 1 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | HDF Sub rack # 1 |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19 |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (to Molex FDU in CuC1) |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12 |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  |  | VU5 |  |  | VU5 |  |  | VU5 |  | VU5 |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  |  | 100mm |  | Front view |  |  |  |  | Rear view |  |  |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [7 empty] | 600mm |  |  |  |  | 600mm |  |  |  | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
[6 empty] | Rear | [6 empty] | Rear
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet 1 |  |  |  |  | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 600D | [5 empty] | 600W x 600D
[6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP5156
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP5156
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 |  |  | VU46 |  |  | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 String(s) |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear View
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP9148
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP9148
Power Base Cabinet Size | 800W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45
Rectifiers per DC System | 2 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  |  | VU43 | AC Power Panel & Meter | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 string(s) |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | None |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear View
|  | 800mm | [6 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP7548
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP7548
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [59 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC +Inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | 10
Expected future maximum power capacity | 10
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 | DC Power System Chassis |  | VU46 | [56 empty] | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 | [56 empty] | VU45 |  | VU45
Rectifiers per DC System | 6 |  |  | VU44 |  |  | VU44 | [56 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 |  |  | VU43 | [56 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 | [56 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 |  |  | VU41 | [56 empty] | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 | [56 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 | [56 empty] | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 6 |  |  | VU38 |  |  | VU38 | [56 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 | [56 empty] | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [56 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [56 empty] | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [56 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [56 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [56 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [56 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [56 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [56 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [56 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [56 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  |  | RSU5 600W x 600D x 2200H |  |  |  |  | RSU6 600W x 600D x 2200H |  |  |  |  | RSU6 600W x 600D x 2200H |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [56 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [56 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [56 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [56 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [56 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [56 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [56 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [56 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [56 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [56 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [56 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [56 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [56 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [56 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | 174.3 |  |  | VU11 |  |  | VU11 | [56 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | 156.9 |  |  | VU10 |  |  | VU10 | [56 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | 191.7 |  |  | VU9 |  |  | VU9 | [56 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [56 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [56 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [56 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [56 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [56 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [56 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [56 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [56 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | RSU6
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2560
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2560
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [7 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [7 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  |  | VU46 |  |  |  | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  |  | VU45 |  |  |  | VU45 |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  |  | VU41 |  |  |  | VU41 |  | VU41
|  |  |  | VU40 |  |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Not Required |  |  | VU37 |  |  |  | VU37 |  |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 1 |  |  | VU33 |  |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 3 |  |  | VU32 |  |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 | HDF Sub rack # 1 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 | MDF Tie # 1 | MDF Tie # 2 | MDF Tie # 3 | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  |  | VU10 |  |  |  | VU10 |  | VU10
|  |  |  | VU9 |  |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  |  | VU8 |  |  |  | VU8 |  | VU8
Customer has requested HDF subrack in VU15 |  |  |  | VU7 |  |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [7 empty] | Rear view
|  | 600mm | [7 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [8 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4521
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4521
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | Fixing bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | HDF sub-racks in Power Base |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
|  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP4564
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP4564
Power Base Cabinet Size | 2 x 600W x 600D |  |  | Standard superstructure assembly | [70 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC +Inverter (1500VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet #1 600W x 600D | [5 empty] | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Customer RSU (600W x 600D) |  |  |  |  | Power Base Cabinet #2 600W x 600D | [5 empty] | Power Base Cabinet #2 600W x 600D |  |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 6800D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Customer RSU (600W x 600D) |  |  |  | Power Base Cabinet #1 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Front view |  | R |  |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 | DC Power System Chassis |  | VU46 | [32 empty] | VU46 | DC Power System Chassis |  | VU46 |  |  | VU46 | AC Power Panel & Meter | VU46 | [26 empty] | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 2 |  |  | VU45 |  |  | VU45 | [32 empty] | VU45 |  |  | VU45 |  |  | VU45 |  | VU45 | [26 empty] | VU45 |  | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 | [32 empty] | VU44 |  |  | VU44 |  |  | VU44 |  | VU44 | [26 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [32 empty] | VU43 |  |  | VU43 |  |  | VU43 |  | VU43 | [26 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 in Power Base #1 only |  |  | VU42 |  |  | VU42 | [32 empty] | VU42 |  |  | VU42 |  |  | VU42 |  | VU42 | [26 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 3 string(s) |  |  | VU41 |  |  | VU41 | [32 empty] | VU41 |  |  | VU41 |  |  | VU41 |  | VU41 | [26 empty] | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 | [32 empty] | VU40 | Nil Inverter Chassis |  | VU40 |  |  | VU40 |  | VU40 | [26 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 | [32 empty] | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39 | [26 empty] | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 6 |  |  | VU38 |  |  | VU38 | [32 empty] | VU38 |  |  | VU38 |  |  | VU38 |  | VU38 | [26 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 | [32 empty] | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37 | [26 empty] | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [32 empty] | VU36 |  |  | VU36 |  |  | VU36 |  | VU36 | [26 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [32 empty] | VU35 |  |  | VU35 |  |  | VU35 |  | VU35 | [26 empty] | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [32 empty] | VU34 |  |  | VU34 |  |  | VU34 |  | VU34 | [26 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [32 empty] | VU33 |  |  | VU33 |  |  | VU33 |  | VU33 | [26 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [32 empty] | VU32 |  |  | VU32 |  |  | VU32 |  | VU32 | [26 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [32 empty] | VU31 |  |  | VU31 |  |  | VU31 |  | VU31 | [26 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [32 empty] | VU30 |  |  | VU30 |  |  | VU30 |  | VU30 | [26 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [32 empty] | VU29 |  |  | VU29 |  |  | VU29 |  | VU29 | [26 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [32 empty] | VU28 |  |  | VU28 |  |  | VU28 |  | VU28 | [26 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [32 empty] | VU27 |  |  | VU27 |  |  | VU27 |  | VU27 | [26 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H |  |  |  |  | RSU2 600W x 600D x 2200H |  |  |  |  | RSU3 600W x 600D x 2200H |  |  |  |  | RSU4 600W x 600D x 2200H |  |  |  |  | RSU5 600W x 600D x 2200H |  |  |  |  | RSU6 600W x 600D x 2200H |  |  |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26 |  |  | RSU6 600W x 600D x 2200H |  |  |  | RSU5 600W x 600D x 2200H |  |  |  | RSU4 600W x 600D x 2200H |  |  |  | RSU3 600W x 600D x 2200H |  |  |  | RSU2 600W x 600D x 2200H |  |  |  | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [32 empty] | VU25 |  |  | VU25 |  |  | VU25 |  | VU25 | [26 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [32 empty] | VU24 |  |  | VU24 |  |  | VU24 |  | VU24 | [26 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [32 empty] | VU23 |  |  | VU23 |  |  | VU23 |  | VU23 | [26 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [32 empty] | VU22 |  |  | VU22 |  |  | VU22 |  | VU22 | [26 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [32 empty] | VU21 |  |  | VU21 |  |  | VU21 |  | VU21 | [26 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [32 empty] | VU20 |  |  | VU20 |  |  | VU20 |  | VU20 | [26 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 | [32 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) |  | VU19 |  |  | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19 | [26 empty] | VU19 | BATTERY ENCLOSURE #3 - (all access from front) | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [32 empty] | VU18 |  |  | VU18 |  |  | VU18 |  | VU18 | [26 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [32 empty] | VU17 |  |  | VU17 |  |  | VU17 |  | VU17 | [26 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [32 empty] | VU16 |  |  | VU16 |  |  | VU16 |  | VU16 | [26 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [32 empty] | VU15 |  |  | VU15 |  |  | VU15 |  | VU15 | [26 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [32 empty] | VU14 |  |  | VU14 |  |  | VU14 |  | VU14 | [26 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [32 empty] | VU13 |  |  | VU13 |  |  | VU13 |  | VU13 | [26 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 | [32 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12 | [26 empty] | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [32 empty] | VU11 |  |  | VU11 |  |  | VU11 |  | VU11 | [26 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [32 empty] | VU10 |  |  | VU10 |  |  | VU10 |  | VU10 | [26 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [32 empty] | VU9 |  |  | VU9 |  |  | VU9 |  | VU9 | [26 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [32 empty] | VU8 |  |  | VU8 |  |  | VU8 |  | VU8 | [26 empty] | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 | [32 empty] | VU7 |  |  | VU7 |  |  | VU7 |  | VU7 | [26 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [32 empty] | VU6 |  |  | VU6 |  |  | VU6 |  | VU6 | [26 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [32 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5 | [26 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [32 empty] | VU4 |  |  | VU4 |  |  | VU4 |  | VU4 | [26 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [32 empty] | VU3 |  |  | VU3 |  |  | VU3 |  | VU3 | [26 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [32 empty] | VU2 |  |  | VU2 |  |  | VU2 |  | VU2 | [26 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [32 empty] | VU1 |  |  | VU1 |  |  | VU1 |  | VU1 | [26 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view |  |  |  |  | Front view | [5 empty] | Front View | [5 empty] | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm |  |  |  |  | 600mm | [5 empty] | 600mm |  |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
[6 empty] | Rear | [35 empty] | Rear
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post) |  |  |  |  | Power Base Cabinet #1 | [35 empty] | Power Base Cabinet #2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF | [10 empty] | RSU1 |  |  |  |  | RSU2 |  |  |  |  | RSU3 |  |  |  |  | RSU4 |  |  |  |  | RSU5 |  |  |  |  | RSU6
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D |  |  |  |  | 600W x 600D | [5 empty] | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front | [35 empty] | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP6615
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP)
FCP Template Code | FCP6615
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [5 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC + inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 |  |  | VU45 |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 1 |  |  | VU43 | DC Power System Chassis |  | VU43 |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 |  |  | VU41 |  |  | VU41 |  | VU41
|  |  |  | VU40 | Inverter Chassis |  | VU40 |  |  | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  | VU35 |  | VU35
Openreach HDF option requirement | Not required |  |  | VU34 |  |  | VU34 |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A |  |  | VU21 |  |  | VU21 |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A |  |  | VU20 |  |  | VU20 |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A |  |  | VU19 |  |  | VU19 |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A |  |  | VU18 |  |  | VU18 |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [5 empty] | Rear View
|  | 600mm | [5 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Signifies FCP structure (cable management system and vertical post)
Power Base Cabinet
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 600W x 600D
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP1222
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT and REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP1222
Power Base Cabinet Size | 600W x 800D |  |  | Standard superstructure assembly | [6 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC only Standard System
Standby AC power | ESS (default) | Power Base Cabinet 600W x 800D | [6 empty] | Power Base Cabinet 600W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | refer to APO order / job pack |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 0 |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  | VU45
Rectifiers per DC System | 0 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 | AC Power Panel & Meter | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 0 |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 600W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 0 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Not Required |  |  | VU37 |  |  | VU37 |  |  |  | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | not required |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  | VU12
Load current major alarm setting (A) | N/A |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) | N/A |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  | VU10
|  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View | [6 empty] | Rear view
|  | 600mm | [6 empty] | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
Rear
FCP AC Panel (used in all Power Base Cabinets)
Power Base Cabinet
Signifies FCP structure (cable management system and vertical post)
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
600W x 800D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted | [7 empty] | End of diagram
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP2695
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm) | [10 empty] | REAR ELEVATION VIEWS BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP2695
Power Base Cabinet Size | 600W x 600D |  |  | Standard superstructure assembly | [15 empty] | Standard superstructure assembly
AC & DC Power Services Required | AC+Std DC+Inverter(750VA n+1)
Standby AC power | ESS (default) | Power Base Cabinet 600W x 600D | [5 empty] | Customer RSU1 (600W x 600D) | [5 empty] | Customer RSU1(600W x 600D) |  |  |  | Power Base Cabinet 600W x 600D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  | L | Front view |  | R |  |  | L | Rear view | R |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO order / job pack
Expected future maximum power capacity | refer to APO order / job pack
AC Supply type (actual design is subject to BT survey) | Three Line (phase) |  |  | VU46 | DC Power System Chassis |  | VU46 | [12 empty] | VU46 | AC Power Panel & Meter | VU46
Number of DC Systems provided | 1 |  |  | VU45 |  |  | VU45 | [12 empty] | VU45 |  | VU45
Rectifiers per DC System | 3 |  |  | VU44 |  |  | VU44 | [12 empty] | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 | [12 empty] | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 0 |  |  | VU42 |  |  | VU42 | [12 empty] | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 1 String(s) |  |  | VU41 |  |  | VU41 | [12 empty] | VU41 |  | VU41
|  |  |  | VU40 | Inverter chassis |  | VU40 | [12 empty] | VU40 |  | VU40
Customer RSU size | 600W x 600D |  |  | VU39 | 16-Way Molex DC sub-distribution module |  | VU39 | [12 empty] | VU39 | AC PDU & Flex tie bar | VU39
Quantity of Customer RSUs | 1 |  |  | VU38 |  |  | VU38 | [12 empty] | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 | Fixing Bar |  | VU37 | [12 empty] | VU37 | Fixing Bar | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 | [12 empty] | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 | [12 empty] | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 | [12 empty] | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 | [12 empty] | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 | [12 empty] | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 | [12 empty] | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 | [12 empty] | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 | [12 empty] | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 | [12 empty] | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 | [12 empty] | VU27 |  | VU27
Customer Use Cabinets with doors | 0 |  |  | VU26 |  |  | VU26 |  |  | RSU1 600W x 600D x 2200H | [5 empty] | RSU1 600W x 600D x 2200H |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 | [12 empty] | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 | [12 empty] | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 0 |  |  | VU23 |  |  | VU23 | [12 empty] | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 | [12 empty] | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 | [12 empty] | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 | [12 empty] | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 | [12 empty] | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 | [12 empty] | VU18 |  | VU18
Ways 5 & 13 | 40A (default) |  |  | VU17 |  |  | VU17 | [12 empty] | VU17 |  | VU17
Ways 6 & 14 | 40A (default) |  |  | VU16 |  |  | VU16 | [12 empty] | VU16 |  | VU16
Ways 7 & 15 | 40A (default) |  |  | VU15 |  |  | VU15 | [12 empty] | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 | [12 empty] | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 | [12 empty] | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 |  |  | VU12 | [12 empty] | VU12 |  | VU12
Load current major alarm setting (A) | refer to APO order / job pack |  |  | VU11 |  |  | VU11 | [12 empty] | VU11 |  | VU11
Load current minor alarm setting (A) | refer to APO order / job pack |  |  | VU10 |  |  | VU10 | [12 empty] | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) | refer to APO order / job pack |  |  | VU9 |  |  | VU9 | [12 empty] | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 | [12 empty] | VU8 |  | VU8
MDF ties to be terminated in the customer provided cabinet |  |  |  | VU7 |  |  | VU7 | [12 empty] | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 | [12 empty] | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 | [12 empty] | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 | [12 empty] | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 | [12 empty] | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 | [12 empty] | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 | [12 empty] | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | Front View |  |  |  |  | Front view | [5 empty] | Rear view |  |  |  |  | Rear view
|  | 600mm | [5 empty] | 600mm | [5 empty] | 600mm |  |  |  | 600mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets)
Rear
Signifies FCP structure (cable management system and vertical post) | [5 empty] | Power Base Cabinet
RSU 1
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
[6 empty] | 600W x 600D |  |  |  |  | 600W x 600D
Customer Use Cabinet' (CuC) Option |  |  |  |  | Front
PLAN VIEW
Optional 16-way Molex or 6-way AC PDU options within CuC
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts

## FCP0394
Click to RETURN TO FCP INDEX
FCP Build Dimensioning Overview (Eltek FCP) |  | FRONT ELEVATION VIEW BELOW (All dimensions are in millimetres - mm) | [20 empty] | REAR ELEVATION VIEW BELOW (All dimensions are in millimetres - mm)
FCP Template Code | FCP0394
Power Base Cabinet Size | 800W x 800D
AC & DC Power Services Required | AC+Std DC+Inverter(1500VA n+1) |  |  |  |  | Standard superstructure assembly | [31 empty] | Standard superstructure assembly
Standby AC power | ESS (default) | Power Base Cabinet 800W x 800D | [6 empty] | Customer Use Cabinet in RSU1 800W x 800D | [6 empty] | Customer Use Cabinet in RSU2 800W x 800D | [7 empty] | Customer Use Cabinet in RSU2 800W x 800D | [5 empty] | Customer Use Cabinet in RSU1 800W x 800D | [5 empty] | Power Base Cabinet 800W x 800D
Electricity metering | Metered (default) |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  | L | Front view |  | R |  |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R |  |  |  | L | Rear view | R
Initial maximum power capacity | refer to APO Order / Job Pack |  | Cable riser for Openreach Ties and fibre cables only | VU48 |  |  | VU48 | Cable riser for Customer cabling only |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar |  | VU48 |  |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  |  | VU48 | AC PDU & Flex tie bar | VU48 |  |  | Cable riser for Customer cabling only | VU48 |  | VU48 | Cable riser for Openreach Ties and fibre cables only
Expected future maximum power capacity | refer to APO Order / Job Pack |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  | VU47 |  |  | VU47 |  |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47 |  |  |  | VU47 |  | VU47
AC Supply type (actual design is subject to BT survey) | Three Line(phase) |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  | VU46 |  |  | VU46 |  |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46 |  |  |  | VU46 |  | VU46
Number of DC Systems provided | 1 |  |  | VU45 | DC Power System Chassis |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  | VU45 |  |  | VU45 |  |  |  |  | VU45 |  | VU45 |  |  |  | VU45 |  | VU45 |  |  |  | VU45 | AC Power Panel & Meter | VU45
Rectifiers per DC System | 4 |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  | VU44 |  |  | VU44 |  |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44 |  |  |  | VU44 |  | VU44
Inverter chassis 750VA n+1 (2 modules) | 0 |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  | VU43 |  |  | VU43 |  |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43 |  |  |  | VU43 |  | VU43
Inverter chassis 1500VA n+1 (3 modules) | 1 |  |  | VU42 | Inverter Chassis |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  | VU42 |  |  | VU42 |  |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42 |  |  |  | VU42 |  | VU42
SBSC11 Battery strings per Power Base Cabinet | 2 string(s) |  |  | VU41 | 16-Way Molex DC sub-distribution module |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  | VU41 |  |  | VU41 |  |  |  |  | VU41 |  | VU41 |  |  |  | VU41 |  | VU41 |  |  |  | VU41 | AC PDU & Flex tie bar | VU41
|  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  | VU40 |  |  | VU40 |  |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40 |  |  |  | VU40 |  | VU40
Customer RSU size | 800W x 800D |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  | VU39 |  |  | VU39 |  |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39 |  |  |  | VU39 |  | VU39
Quantity of Customer RSUs | 2 |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  | VU38 |  |  | VU38 |  |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38 |  |  |  | VU38 |  | VU38
Lockable Door Option - 'AC only' Power Base & HDF cabinets | Doors standard with DC option |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  | VU37 |  |  | VU37 |  |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37 |  |  |  | VU37 |  | VU37
Note: All Power Base cabinets supplied with DC power are fitted with lockable doors as standard. |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  | VU36 |  |  | VU36 |  |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36 |  |  |  | VU36 |  | VU36
|  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  | VU35 |  |  | VU35 |  |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35 |  |  |  | VU35 |  | VU35
Openreach HDF option requirement | 0 |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  | VU34 |  |  | VU34 |  |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34 |  |  |  | VU34 |  | VU34
HDF Sub racks provided | 0 |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  | VU33 |  |  | VU33 |  |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33 |  |  |  | VU33 |  | VU33
Expected future maximum tie cables | 0 |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  | VU32 |  |  | VU32 |  |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32 |  |  |  | VU32 |  | VU32
Initial LLUT tie cables required | 0 |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  | VU31 |  |  | VU31 |  |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31 |  |  |  | VU31 |  | VU31
Initial LLUL tie cables required | 0 |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  | VU30 |  |  | VU30 |  |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30 |  |  |  | VU30 |  | VU30
Initial LLUX tie cables required | 0 |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  | VU29 |  |  | VU29 |  |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29 |  |  |  | VU29 |  | VU29
Initial LLUY tie cables required | 0 |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  | VU28 |  |  | VU28 |  |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28 |  |  |  | VU28 |  | VU28
|  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  | VU27 |  |  | VU27 |  |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27 |  |  |  | VU27 |  | VU27
Customer Use Cabinets with doors | 2 |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  | VU26 |  |  | VU26 |  |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26 |  |  |  | VU26 |  | VU26
16-Way Molex FDU in each CuC | 0 |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  | VU25 |  |  | VU25 |  |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25 |  |  |  | VU25 |  | VU25
6-Way IEC AC PDU in each CuC | 0 |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  | VU24 |  |  | VU24 |  |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24 |  |  |  | VU24 |  | VU24
6-Way AC PDU (3-pin socket outlets) in each CuC | 2 |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  | VU23 |  |  | VU23 |  |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23 |  |  |  | VU23 |  | VU23
DC Power System Option - MCB Customisation |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  | VU22 |  |  | VU22 |  |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22 |  |  |  | VU22 |  | VU22
Ways 1 & 9 | 63A (default) |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  | VU21 |  |  | VU21 |  |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21 |  |  |  | VU21 |  | VU21
Ways 2 & 10 | 63A (default) |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  | VU20 |  |  | VU20 |  |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20 |  |  |  | VU20 |  | VU20
Ways 3 & 11 | 63A (default) |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  | VU19 |  |  | VU19 |  |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19 |  |  |  | VU19 |  | VU19
Ways 4 & 12 | 63A (default) |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  | VU18 |  |  | VU18 |  |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18 |  |  |  | VU18 |  | VU18
Ways 5 & 13 | 40A |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  | VU17 |  |  | VU17 |  |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17 |  |  |  | VU17 |  | VU17
Ways 6 & 14 | 40A |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  | VU16 |  |  | VU16 |  |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16 |  |  |  | VU16 |  | VU16
Ways 7 & 15 | 40A |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  | VU15 |  |  | VU15 |  |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15 |  |  |  | VU15 |  | VU15
Ways 8 & 16 serve Power Base mounted 16-Way Molex FDU | 40A |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  | VU14 |  |  | VU14 |  |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14 |  |  |  | VU14 |  | VU14
|  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  | VU13 |  |  | VU13 |  |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13 |  |  |  | VU13 |  | VU13
DC Power System Option - Alarm settings - based on initial maximum power capacity |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  | VU12 |  |  | VU12 |  |  |  |  | VU12 |  | VU12 |  |  |  | VU12 |  | VU12 |  |  |  | VU12 | BATTERY ENCLOSURE #2 - (all access from front) | VU12
Load current major alarm setting (A) | refer to APO order / job pack then use Alarm and current settings sheet within Matrix |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  | VU11 |  |  | VU11 |  |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11 |  |  |  | VU11 |  | VU11
Load current minor alarm setting (A) |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  | VU10 |  |  | VU10 |  |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10 |  |  |  | VU10 |  | VU10
Rectifier current limit setting on each installed Power Base in a PoP (A) |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  | VU9 |  |  | VU9 |  |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9 |  |  |  | VU9 |  | VU9
Additional customer requirements |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  | VU8 |  |  | VU8 |  |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8 |  |  |  | VU8 |  | VU8
|  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  | VU7 |  |  | VU7 |  |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7 |  |  |  | VU7 |  | VU7
|  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  | VU6 |  |  | VU6 |  |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6 |  |  |  | VU6 |  | VU6
|  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  | VU5 |  |  | VU5 |  |  |  |  | VU5 |  | VU5 |  |  |  | VU5 |  | VU5 |  |  |  | VU5 | BATTERY ENCLOSURE #1 - (all access from front) | VU5
|  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  | VU4 |  |  | VU4 |  |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4 |  |  |  | VU4 |  | VU4
|  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  | VU3 |  |  | VU3 |  |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3 |  |  |  | VU3 |  | VU3
|  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  | VU2 |  |  | VU2 |  |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2 |  |  |  | VU2 |  | VU2
|  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  | VU1 |  |  | VU1 |  |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1 |  |  |  | VU1 |  | VU1
Key to colour scheme used in layout diagrams: |  |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  | 100mm | Front view |  |  |  | 100mm |  |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm |  | 100mm | Rear view |  |  | 100mm
|  | 800mm | [6 empty] | 800mm | [6 empty] | 800mm | [7 empty] | 800mm | [5 empty] | 800mm | [5 empty] | 800mm
Power Base Cabinet(s) provided as part of the FCP build order
FCP AC Panel (used in all Power Base Cabinets) | [5 empty] | Rear | [6 empty] | Rear | [6 empty] | Rear
|  |  | Openreach Cabling riser |  |  |  |  | Customer cabling only
Signifies FCP structure (cable management system and vertical post)
[6 empty] | Power Base Cabinet |  |  |  |  | Customer Use Cabinet on RSU 1 | [6 empty] | Customer Use Cabinet on RSU 2
800mm wide HDF rack cable riser to be used for Openreach copper tie cables from MDF
800mm wide Power Base cabinet cable riser to be used for Openreach copper tie cables from MDF and ethernet fibre cable (unless customer requests otherwise).
600mm wide cabinet cable routeing channel for Openreach copper tie cables and fibre cables (unless customer requests otherwise)
Routeing of incoming Openreach tie cabling from MDF
FCP DC Power System Option Components
Customer Use Cabinet' (CuC) Option | [5 empty] | 800W x 800D | [5 empty] | 800W x 800D | [6 empty] | 800W x 800D
[6 empty] | Front | [6 empty] | Front | [6 empty] | Front
Optional 16-way Molex or 6-way AC PDU options within CuC
PLAN VIEW
Denotes cabinet side panels fitted
Customer 'Rack Space Unit' (RSU)
Unused VU positions in Power Base, HDF & CuC are for customer use.
Ethernet fibre and chassis positions are be agreed with the customer at time of ethernet order.
Spare - Denotes Expanded Battery Capacity Cabinet Option
Spare - Denotes Openreach HDF Rack Option
Spare - Denotes HDF Sub-Rack Option
Spare - Denotes Backhaul fibre tray location agreed with customer
Please note: these are indicative layouts and reflect the products in straight single suite line. In all cases please consult the related floor plans to reflect the proposed layouts